## Load Sched
400V
| AMPERE |  |  |  | MULTI | AMPERE TRIP |  |  | KW
| L1 | L2 | L3 | 3 PHASE |  | 1 PHASE | 3 PHASE | OVERALL | 1 PHASE |  | 3 PHASE |  | OVERALL
1 |  | 32.91 |  |  | 1.25 | 41.1375 | 0 | 41.1375 | 7.5693 |  | 0 |  | 7.5693
2 |  |  |  |  | 1.25 | 0 | 0 | - | 0 |  | 0 |  | -
[15 empty] | 1 PHASE |  |  | 3 PHASE | CONNECTED DF
3 |  |  |  |  | 1.25 | 0 | 0 | - | 0 |  | 0 |  | - | [6 empty] | 0.8 | 6.0554
4 |  |  |  |  | 1.25 | 0 | 0 | - | 0 |  | 0 |  | - | KVA | 0 | 7.5693 | 0 | 0 |  | 0.7 | 5.2985
[20 empty] | 0.6 | 4.5416
5 |  |  |  |  | 1.25 | 0 | 0 | - | 0 |  | 0 |  | - | TOTAL KVA | 7.5693 |  |  | 0 |  | 0.52 | 3.936
6 |  |  |  |  | 1.25 | 0 | 0 | - | 0 |  | 0 |  | - | [6 empty] | 0.48 | 3.6333
[14 empty] | OVERALL KVA | 7.5693 |  |  |  |  | 0.29 | 2.1951
7 |  |  |  |  | 1.25 | 0 | 0 | - | 0 |  | 0 |  | - | [6 empty] | 0.2 | 1.5139
8 |  |  |  |  | 1.25 | 0 | 0 | - | 0 |  | 0 |  | -
[19 empty] | TEST | 0.8 | 0
9 |  |  |  |  | 1.25 | 0 | 0 | - | 0 |  | 0 |  | - | [6 empty] | 0.7 | 0
10 |  |  |  |  | 1.25 | 0 | 0 | - | 0 |  | 0 |  | - | TOTAL AT COMPUTATION | [5 empty] | 0.6 | 0
[16 empty] | 1 PHASE | 3 PHASE |  |  | 0.5 | 0
11 |  |  |  |  | 1.25 | 0 | 0 | - | 0 |  | 0 |  | - | [6 empty] | 0.4 | 0
12 |  |  |  |  | 1.25 | 0 | 0 | - | 0 |  | 0 |  | - | AMPERE |  | 32.91 | 0 |  |  | 0.3 | 0
13 |  |  |  |  | 1.25 | 0 | 0 | - | 0 |  | 0 |  | - | TOTAL AMPERE |  | 32.91
14 |  |  |  |  | 1.25 | 0 | 0 | - | 0 |  | 0 |  | -
[14 empty] | MAINS AT |  | 41.1375 |  |  | MAINS AT x DF
15 |  |  |  |  | 1.25 | 0 | 0 | - | 0 |  | 0 |  | - | [6 empty] | 0.8 | 32.91
16 |  |  |  |  | 1.25 | 0 | 0 | - | 0 |  | 0 |  | - | [6 empty] | 0.7 | 28.7962
[20 empty] | 0.6 | 24.6825
17 |  |  |  |  | 1.25 | 0 | 0 | - | 0 |  | 0 |  | - | [6 empty] | 0.48 | 19.746
18 |  |  |  |  | 1.25 | 0 | 0 | - | 0 |  | 0 |  | - | AT COMPUTATION | [5 empty] | 3 | 123.4125
[15 empty] | SAFETY | AMP | AT |  |  | 0.25 | 10.2844
19 |  |  |  |  | 1.25 | 0 | 0 | - | 0 |  | 0 |  | - | [5 empty] | for units | 0.23 | 9.4616
20 |  |  |  |  | 1.25 | 0 | 0 | - | 0 |  | 0 |  | - | NORMAL LOAD | 1.25 |  | 0
[14 empty] | 1 PHASE ACCU | 2.25 |  | 0 |  | TEST | 0.8 | 0
21 |  |  |  |  | 1.25 | 0 | 0 | - | 0 |  | 0 |  | - | WATER HEATER | 1.5 |  | 0 |  |  | 0.7 | 0
22 |  |  |  |  | 1.25 | 0 | 0 | - | 0 |  | 0 |  | - | EV CHARGER | 1.4 |  | 0 |  |  | 0.6 | 0
[14 empty] | 1PHASE MOTOR | 2.5 |  | 0 |  |  | 0.5 | 0
23 |  |  |  |  | 1.25 | 0 | 0 | - | 0 |  | 0 |  | - | [6 empty] | 0.4 | 0
24 |  |  |  |  | 1.25 | 0 | 0 | - | 0 |  | 0 |  | - | [6 empty] | 0.3 | 0
25 |  |  |  |  | 1.25 | 0 | 0 | - | 0 |  | 0 |  | -
26 |  |  |  |  | 1.25 | 0 | 0 | - | 0 |  | 0 |  | -
27 |  |  |  |  | 1.25 | 0 | 0 | - | 0 |  | 0 |  | -
28 |  |  |  |  | 1.25 | 0 | 0 | - | 0 |  | 0 |  | -
29 |  |  |  |  | 1.25 | 0 | 0 | - | 0 |  | 0 |  | -
30 |  |  |  |  | 1.25 | 0 | 0 | - | 0 |  | 0 |  | -
| 0 | 32.91 | 0 | 0 | 1.25 | 41.1375 | 0 | 41.1375 | 7.5693 |  | 0 |  | 7.5693
400V (KW TO AMP)
| KW |  |  |  | AMPERE |  |  |  | MULTI | AMPERE TRIP
| 1 PHASE | 3 PHASE | OVERALL |  | L1 | L2 | L3 | 3 PHASE |  | 1 PHASE | 3 PHASE | OVERALL
1 |  | 300 | 300 |  | 0 |  |  | 433.0254 | 1.25 | 0 | 541.2818 | 541.2818
2 |  |  | - |  | 0 |  |  | 0 | 1.25 | 0 | 0 | - |  |  | 1 PHASE |  |  | 3 PHASE | CONNECTED DF
[20 empty] | 0.8 | 240
3 |  |  | - |  |  | 0 |  | 0 | 1.25 | 0 | 0 | - |  | KVA | 0 | 0 | 0 | 300 |  | 0.7 | 210
4 |  |  | - |  |  | 0 |  | 0 | 1.25 | 0 | 0 | - | [7 empty] | 0.6 | 180
[14 empty] | TOTAL KVA | 0 |  |  | 300 |  | 0.5 | 150
5 |  |  | - |  |  |  | 0 | 0 | 1.25 | 0 | 0 | - | [7 empty] | 0.4 | 120
6 |  |  | - |  |  |  | 0 | 0 | 1.25 | 0 | 0 | - |  | OVERALL KVA | 300 |  |  |  |  | 0.38 | 114
7 |  |  | - |  | 0 |  |  | 0 | 1.25 | 0 | 0 | -
8 |  |  | - |  | 0 |  |  | 0 | 1.25 | 0 | 0 | - | [6 empty] | TEST | 0.8 | 0
[20 empty] | 0.7 | 0
9 |  |  | - |  |  | 0 |  | 0 | 1.25 | 0 | 0 | - |  | TOTAL AT COMPUTATION | [5 empty] | 0.6 | 0
10 |  |  | - |  |  | 0 |  | 0 | 1.25 | 0 | 0 | - |  |  |  | 1 PHASE | 3 PHASE |  |  | 0.5 | 0
[20 empty] | 0.4 | 0
11 |  |  | - |  |  |  | 0 | 0 | 1.25 | 0 | 0 | - |  | AMPERE |  | 0 | 433.0254 |  |  | 0.3 | 0
12 |  |  | - |  |  |  | 0 | 0 | 1.25 | 0 | 0 | -
[14 empty] | TOTAL AMPERE |  | 433.0254
13 |  |  | - |  | 0 |  |  | 0 | 1.25 | 0 | 0 | -
14 |  |  | - |  | 0 |  |  | 0 | 1.25 | 0 | 0 | - |  | MAINS AT |  | 541.2818 |  |  | MAINS AT x DF
[20 empty] | 0.8 | 433.0254
15 |  |  | - |  |  | 0 |  | 0 | 1.25 | 0 | 0 | - | [7 empty] | 0.7 | 378.8972
16 |  |  | - |  |  | 0 |  | 0 | 1.25 | 0 | 0 | - | [7 empty] | 0.65 | 351.8331
[20 empty] | 0.5 | 270.6409
17 |  |  | - |  |  |  | 0 | 0 | 1.25 | 0 | 0 | - |  | AT COMPUTATION | [5 empty] | 0.4 | 216.5127
18 |  |  | - |  |  |  | 0 | 0 | 1.25 | 0 | 0 | - |  |  | SAFETY | AMP | AT |  |  | 0.38 | 205.6871
[19 empty] | for units | 0.2 | 108.2564
19 |  |  | - |  | 0 |  |  | 0 | 1.25 | 0 | 0 | - |  | NORMAL LOAD | 1.25 | 22.37 | 27.9625
20 |  |  | - |  | 0 |  |  | 0 | 1.25 | 0 | 0 | - |  | 1 PHASE ACCU | 2.25 | 12 | 27 |  | TEST | 0.8 | 0
[14 empty] | WATER HEATER | 2 |  | 0 |  |  | 0.7 | 0
21 |  |  | - |  |  | 0 |  | 0 | 1.25 | 0 | 0 | - |  | EV CHARGER | 1.5 |  | 0 |  |  | 0.6 | 0
22 |  |  | - |  |  | 0 |  | 0 | 1.25 | 0 | 0 | - | [7 empty] | 0.5 | 0
[20 empty] | 0.4 | 0
23 |  |  | - |  |  |  | 0 | 0 | 1.25 | 0 | 0 | - | [7 empty] | 0.3 | 0
24 |  |  | - |  |  |  | 0 | 0 | 1.25 | 0 | 0 | -
25 |  |  | - |  | 0 |  |  | 0 | 1.25 | 0 | 0 | -
26 |  |  | - |  | 0 |  |  | 0 | 1.25 | 0 | 0 | -
27 |  |  | - |  |  | 0 |  | 0 | 1.25 | 0 | 0 | -
28 |  |  | - |  |  | 0 |  | 0 | 1.25 | 0 | 0 | -
29 |  |  | - |  |  |  | 0 | 0 | 1.25 | 0 | 0 | -
30 |  |  | - |  |  |  | 0 | 0 | 1.25 | 0 | 0 | -
| 0 | 300 | 300 |  | 0 | 0 | 0 | 433.0254 | 1.25 | 0 | 541.2818 | 541.2818
230V
| AMPERE |  |  |  | MULTI | AMPERE TRIP |  |  | KW
| L1 | L2 | L3 | 3 PHASE |  | 1 PHASE | 3 PHASE | OVERALL | 1 PHASE |  | 3 PHASE |  | OVERALL
1 |  |  |  | 200 | 1.25 | 0 | 250 | 250 | 0 |  | 79.672 |  | 79.672
2 |  |  |  |  | 1.25 | 0 | 0 | - | 0 |  | 0 |  | -
[15 empty] | 1 PHASE |  |  | 3 PHASE | CONNECTED DF
3 |  |  |  |  | 1.25 | 0 | 0 | - | 0 |  | 0 |  | - | [6 empty] | 0.8 | 63.7376
4 |  |  |  |  | 1.25 | 0 | 0 | - | 0 |  | 0 |  | - | KVA | 0 | 0 | 0 | 79.672 |  | 0.7 | 55.7704
[20 empty] | 0.6 | 47.8032
5 |  |  |  |  | 1.25 | 0 | 0 | - | 0 |  | 0 |  | - | TOTAL KVA | 0 |  |  | 79.672 |  | 0.5 | 39.836
6 |  |  |  |  | 1.25 | 0 | 0 | - | 0 |  | 0 |  | - | [6 empty] | 0.4 | 31.8688
[14 empty] | OVERALL KVA | 79.672 |  |  |  |  | 0.29 | 23.1049
7 |  |  |  |  | 1.25 | 0 | 0 | - | 0 |  | 0 |  | - | [6 empty] | 0.2 | 15.9344
8 |  |  |  |  | 1.25 | 0 | 0 | - | 0 |  | 0 |  | -
[19 empty] | TEST | 0.8 | 0
9 |  |  |  |  | 1.25 | 0 | 0 | - | 0 |  | 0 |  | - | [6 empty] | 0.7 | 0
10 |  |  |  |  | 1.25 | 0 | 0 | - | 0 |  | 0 |  | - | TOTAL AT COMPUTATION | [5 empty] | 0.6 | 0
[16 empty] | 1 PHASE | 3 PHASE |  |  | 0.5 | 0
11 |  |  |  |  | 1.25 | 0 | 0 | - | 0 |  | 0 |  | - | [6 empty] | 0.4 | 0
12 |  |  |  |  | 1.25 | 0 | 0 | - | 0 |  | 0 |  | - | AMPERE |  | 0 | 200 |  |  | 0.3 | 0
13 |  |  |  |  | 1.25 | 0 | 0 | - | 0 |  | 0 |  | - | TOTAL AMPERE |  | 200
14 |  |  |  |  | 1.25 | 0 | 0 | - | 0 |  | 0 |  | -
[14 empty] | MAINS AT |  | 250 |  |  | MAINS AT x DF
15 |  |  |  |  | 1.25 | 0 | 0 | - | 0 |  | 0 |  | - | [6 empty] | 0.8 | 200
16 |  |  |  |  | 1.25 | 0 | 0 | - | 0 |  | 0 |  | - | [6 empty] | 0.7 | 175
[20 empty] | 0.6 | 150
17 |  |  |  |  | 1.25 | 0 | 0 | - | 0 |  | 0 |  | - | [6 empty] | 0.43 | 107.5
18 |  |  |  |  | 1.25 | 0 | 0 | - | 0 |  | 0 |  | - | AT COMPUTATION | [5 empty] | 0.2 | 50
[15 empty] | SAFETY | AMP | AT |  |  | 0.25 | 62.5
19 |  |  |  |  | 1.25 | 0 | 0 | - | 0 |  | 0 |  | - | [5 empty] | for units | 0.23 | 57.5
20 |  |  |  |  | 1.25 | 0 | 0 | - | 0 |  | 0 |  | - | NORMAL LOAD | 1.25 |  | 0
[14 empty] | 1 PHASE ACCU | 2.25 |  | 0 |  | TEST | 0.8 | 0
21 |  |  |  |  | 1.25 | 0 | 0 | - | 0 |  | 0 |  | - | WATER HEATER | 1.5 |  | 0 |  |  | 0.7 | 0
22 |  |  |  |  | 1.25 | 0 | 0 | - | 0 |  | 0 |  | - | EV CHARGER | 1.4 |  | 0 |  |  | 0.6 | 0
[14 empty] | 1PHASE MOTOR | 2.5 |  | 0 |  |  | 0.5 | 0
23 |  |  |  |  | 1.25 | 0 | 0 | - | 0 |  | 0 |  | - | [6 empty] | 0.4 | 0
24 |  |  |  |  | 1.25 | 0 | 0 | - | 0 |  | 0 |  | - | [6 empty] | 0.3 | 0
25 |  |  |  |  | 1.25 | 0 | 0 | - | 0 |  | 0 |  | -
26 |  |  |  |  | 1.25 | 0 | 0 | - | 0 |  | 0 |  | -
27 |  |  |  |  | 1.25 | 0 | 0 | - | 0 |  | 0 |  | -
28 |  |  |  |  | 1.25 | 0 | 0 | - | 0 |  | 0 |  | -
29 |  |  |  |  | 1.25 | 0 | 0 | - | 0 |  | 0 |  | -
30 |  |  |  |  | 1.25 | 0 | 0 | - | 0 |  | 0 |  | -
| 0 | 0 | 0 | 200 | 1.25 | 0 | 250 | 250 | 0 |  | 79.672 |  | 79.672
230V (KW TO AMP)
| KW |  |  |  | AMPERE |  |  |  | MULTI | AMPERE TRIP
| 1 PHASE | 3 PHASE | OVERALL |  | L1 | L2 | L3 | 3 PHASE |  | 1 PHASE | 3 PHASE | OVERALL
1 | 1 | 500 | 501 |  | 4.3478 |  |  | 1255.1461 | 1.25 | 5.4348 | 1568.9326 | 1578.3457
2 | 1 | 1 | 2 |  | 4.3478 |  |  | 2.5103 | 1.25 | 5.4348 | 3.1379 | 12.5509 |  |  | 1 PHASE |  |  | 3 PHASE | CONNECTED DF
[20 empty] | 0.8 | 403.872
3 | 0.23 |  | 0.23 |  |  | 1 |  | 0 | 1.25 | 1.25 | 0 | 2.165 |  | KVA | 2 | 0.23 | 0.23 | 502.38 |  | 0.7 | 353.388
4 |  | 0.69 | 0.69 |  |  | 0 |  | 1.7321 | 1.25 | 0 | 2.1651 | 2.1651 | [7 empty] | 0.6 | 302.904
[14 empty] | TOTAL KVA | 2.46 |  |  | 502.38 |  | 0.5 | 252.42
5 | 0.23 | 0.69 | 0.92 |  |  |  | 1 | 1.7321 | 1.25 | 1.25 | 2.1651 | 4.3301 | [7 empty] | 0.4 | 201.936
6 |  |  | - |  |  |  | 0 | 0 | 1.25 | 0 | 0 | - |  | OVERALL KVA | 504.84 |  |  |  |  | 0.38 | 191.8392
7 |  |  | - |  | 0 |  |  | 0 | 1.25 | 0 | 0 | -
8 |  |  | - |  | 0 |  |  | 0 | 1.25 | 0 | 0 | - | [6 empty] | TEST | 0.8 | 0
[20 empty] | 0.7 | 0
9 |  |  | - |  |  | 0 |  | 0 | 1.25 | 0 | 0 | - |  | TOTAL AT COMPUTATION | [5 empty] | 0.6 | 0
10 |  |  | - |  |  | 0 |  | 0 | 1.25 | 0 | 0 | - |  |  |  | 1 PHASE | 3 PHASE |  |  | 0.5 | 0
[20 empty] | 0.4 | 0
11 |  |  | - |  |  |  | 0 | 0 | 1.25 | 0 | 0 | - |  | AMPERE |  | 8.6957 | 1261.1206 |  |  | 0.3 | 0
12 |  |  | - |  |  |  | 0 | 0 | 1.25 | 0 | 0 | -
[14 empty] | TOTAL AMPERE |  | 1276.1815
13 |  |  | - |  | 0 |  |  | 0 | 1.25 | 0 | 0 | -
14 |  |  | - |  | 0 |  |  | 0 | 1.25 | 0 | 0 | - |  | MAINS AT |  | 1595.2268 |  |  | MAINS AT x DF
[20 empty] | 0.8 | 1276.1815
15 |  |  | - |  |  | 0 |  | 0 | 1.25 | 0 | 0 | - | [7 empty] | 0.7 | 1116.6588
16 |  |  | - |  |  | 0 |  | 0 | 1.25 | 0 | 0 | - | [7 empty] | 0.65 | 1036.8974
[20 empty] | 0.5 | 797.6134
17 |  |  | - |  |  |  | 0 | 0 | 1.25 | 0 | 0 | - |  | AT COMPUTATION | [5 empty] | 0.4 | 638.0907
18 |  |  | - |  |  |  | 0 | 0 | 1.25 | 0 | 0 | - |  |  | SAFETY | AMP | AT |  |  | 0.38 | 606.1862
[19 empty] | for units | 0.2 | 319.0454
19 |  |  | - |  | 0 |  |  | 0 | 1.25 | 0 | 0 | - |  | NORMAL LOAD | 1.25 |  | 0
20 |  |  | - |  | 0 |  |  | 0 | 1.25 | 0 | 0 | - |  | 1 PHASE ACCU | 2.25 |  | 0 |  | TEST | 0.8 | 0
[14 empty] | WATER HEATER | 2 |  | 0 |  |  | 0.7 | 0
21 |  |  | - |  |  | 0 |  | 0 | 1.25 | 0 | 0 | - |  | EV CHARGER | 1.5 |  | 0 |  |  | 0.6 | 0
22 |  |  | - |  |  | 0 |  | 0 | 1.25 | 0 | 0 | - | [7 empty] | 0.5 | 0
[20 empty] | 0.4 | 0
23 |  |  | - |  |  |  | 0 | 0 | 1.25 | 0 | 0 | - | [7 empty] | 0.3 | 0
24 |  |  | - |  |  |  | 0 | 0 | 1.25 | 0 | 0 | -
25 |  |  | - |  | 0 |  |  | 0 | 1.25 | 0 | 0 | -
26 |  |  | - |  | 0 |  |  | 0 | 1.25 | 0 | 0 | -
27 |  |  | - |  |  | 0 |  | 0 | 1.25 | 0 | 0 | -
28 |  |  | - |  |  | 0 |  | 0 | 1.25 | 0 | 0 | -
29 |  |  | - |  |  |  | 0 | 0 | 1.25 | 0 | 0 | -
30 |  |  | - |  |  |  | 0 | 0 | 1.25 | 0 | 0 | -
| 2.46 | 502.38 | 504.84 |  | 8.6957 | 1 | 1 | 1261.1206 | 1.25 | 10.8696 | 1576.4007 | 1595.2268
230V - 1 PHASE
|  | AMPERE |  |  | MULTI | AT |  |  | KW
|  | 1 PHASE |  |  |  | 1 PHASE |  |  | 1 PHASE
1 |  | 14.5 |  |  | 1.25 | 18.125 |  |  | 3.335
2 |  | 15.22 |  |  | 1.25 | 19.025 |  |  | 3.5006
[15 empty] | 1 PHASE |  |  |  | CONNECTED DF
3 |  | 2.17 |  |  | 1.25 | 2.7125 |  |  | 0.4991 | [10 empty] | 0.8 | 6.5964
4 |  | 3.13 |  |  | 1.25 | 3.9125 |  |  | 0.7199 |  |  |  |  | KVA |  | 8.2455 |  |  |  | 0.7 | 5.7718
[20 empty] | 0.6 | 4.9473
5 |  | 0.83 |  |  | 1.25 | 1.0375 |  |  | 0.1909 | [10 empty] | 0.5 | 4.1227
6 |  |  |  |  | 1.25 | 0 |  |  | 0 | [10 empty] | 0.4 | 3.2982
[20 empty] | 0.29 | 2.3912
7 |  |  |  |  | 1.25 | 0 |  |  | 0 | [10 empty] | 0.2 | 1.6491
8 |  |  |  |  | 1.25 | 0 |  |  | 0
[19 empty] | TEST | 0.8 | 0
9 |  |  |  |  | 1.25 | 0 |  |  | 0 | [10 empty] | 0.7 | 0
10 |  |  |  |  | 1.25 | 0 |  |  | 0 |  |  |  |  | TOTAL AT COMPUTATION | [5 empty] | 0.6 | 0
[16 empty] | 1 PHASE |  |  |  | 0.5 | 0
11 |  |  |  |  | 1.25 | 0 |  |  | 0 | [10 empty] | 0.4 | 0
12 |  |  |  |  | 1.25 | 0 |  |  | 0 |  |  |  |  | AMPERE |  | 35.85 |  |  |  | 0.3 | 0
13 |  |  |  |  | 1.25 | 0 |  |  | 0
14 |  |  |  |  | 1.25 | 0 |  |  | 0
[14 empty] | MAINS AT |  | 44.8125 |  |  | MAINS AT x DF
15 |  |  |  |  | 1.25 | 0 |  |  | 0 | [10 empty] | 0.8 | 35.85
16 |  |  |  |  | 1.25 | 0 |  |  | 0 | [10 empty] | 0.7 | 31.3687
[20 empty] | 0.6 | 26.8875
17 |  |  |  |  | 1.25 | 0 |  |  | 0 | [10 empty] | 0.43 | 19.2694
18 |  |  |  |  | 1.25 | 0 |  |  | 0 |  |  |  |  | AT COMPUTATION | [5 empty] | 0.2 | 8.9625
[15 empty] | SAFETY | AMP | AT |  |  | 0.25 | 11.2031
19 |  |  |  |  | 1.25 | 0 |  |  | 0 | [9 empty] | for units | 0.23 | 10.3069
20 |  |  |  |  | 1.25 | 0 |  |  | 0 |  |  |  |  | NORMAL LOAD | 1.25 |  | 0
[14 empty] | 1 PHASE ACCU | 2.25 |  | 0 |  | TEST | 0.8 | 0
21 |  |  |  |  | 1.25 | 0 |  |  | 0 |  |  |  |  | WATER HEATER | 1.5 |  | 0 |  |  | 0.7 | 0
22 |  |  |  |  | 1.25 | 0 |  |  | 0 |  |  |  |  | EV CHARGER | 1.4 |  | 0 |  |  | 0.6 | 0
[14 empty] | 1PHASE MOTOR | 2.5 |  | 0 |  |  | 0.5 | 0
23 |  |  |  |  | 1.25 | 0 |  |  | 0 | [10 empty] | 0.4 | 0
24 |  |  |  |  | 1.25 | 0 |  |  | 0 | [10 empty] | 0.3 | 0
25 |  |  |  |  | 1.25 | 0 |  |  | 0
26 |  |  |  |  | 1.25 | 0 |  |  | 0
27 |  |  |  |  | 1.25 | 0 |  |  | 0
28 |  |  |  |  | 1.25 | 0 |  |  | 0
29 |  |  |  |  | 1.25 | 0 |  |  | 0
30 |  |  |  |  | 1.25 | 0 |  |  | 0
|  | 35.85 |  |  | 1.25 | 44.8125 |  |  | 8.2455
230V- 1 PHASE (KW TO AMP)
|  | KW |  |  | AMPERE |  |  |  | MULTI | AT
|  | 1 PHASE |  |  | L1 |  |  |  |  | 1 PHASE
1 |  | 1 |  |  | 4.3478 |  |  |  | 1.25 | 5.4348
2 |  | 1 |  |  | 4.3478 |  |  |  | 1.25 | 5.4348
[15 empty] | 1 PHASE |  |  |  | CONNECTED DF
3 |  | 0.23 |  |  | 1 |  |  |  | 1.25 | 1.25 | [9 empty] | 0.8 | 1.968
4 |  |  |  |  | 0 |  |  |  | 1.25 | 0 |  |  |  | KVA |  | 2.46 |  |  |  | 0.7 | 1.722
[20 empty] | 0.6 | 1.476
5 |  | 0.23 |  |  | 1 |  |  |  | 1.25 | 1.25 | [9 empty] | 0.5 | 1.23
6 |  |  |  |  | 0 |  |  |  | 1.25 | 0 | [9 empty] | 0.4 | 0.984
[20 empty] | 0.29 | 0.7134
7 |  |  |  |  | 0 |  |  |  | 1.25 | 0 | [9 empty] | 0.2 | 0.492
8 |  |  |  |  | 0 |  |  |  | 1.25 | 0
[19 empty] | TEST | 0.8 | 0
9 |  |  |  |  | 0 |  |  |  | 1.25 | 0 | [9 empty] | 0.7 | 0
10 |  |  |  |  | 0 |  |  |  | 1.25 | 0 |  |  |  | TOTAL AT COMPUTATION | [5 empty] | 0.6 | 0
[16 empty] | 1 PHASE |  |  |  | 0.5 | 0
11 |  |  |  |  | 0 |  |  |  | 1.25 | 0 | [9 empty] | 0.4 | 0
12 |  |  |  |  | 0 |  |  |  | 1.25 | 0 |  |  |  | AMPERE |  | 10.6957 |  |  |  | 0.3 | 0
13 |  |  |  |  | 0 |  |  |  | 1.25 | 0
14 |  |  |  |  | 0 |  |  |  | 1.25 | 0
[14 empty] | MAINS AT |  | 13.3696 |  |  | MAINS AT x DF
15 |  |  |  |  | 0 |  |  |  | 1.25 | 0 | [9 empty] | 0.8 | 10.6957
16 |  |  |  |  | 0 |  |  |  | 1.25 | 0 | [9 empty] | 0.7 | 9.3587
[20 empty] | 0.6 | 8.0217
17 |  |  |  |  | 0 |  |  |  | 1.25 | 0 | [9 empty] | 0.43 | 5.7489
18 |  |  |  |  | 0 |  |  |  | 1.25 | 0 |  |  |  | AT COMPUTATION | [5 empty] | 0.2 | 2.6739
[15 empty] | SAFETY | AMP | AT |  |  | 0.25 | 3.3424
19 |  |  |  |  | 0 |  |  |  | 1.25 | 0 | [8 empty] | for units | 0.23 | 3.075
20 |  |  |  |  | 0 |  |  |  | 1.25 | 0 |  |  |  | NORMAL LOAD | 1.25 |  | 0
[14 empty] | 1 PHASE ACCU | 2.25 |  | 0 |  | TEST | 0.8 | 0
21 |  |  |  |  | 0 |  |  |  | 1.25 | 0 |  |  |  | WATER HEATER | 1.5 |  | 0 |  |  | 0.7 | 0
22 |  |  |  |  | 0 |  |  |  | 1.25 | 0 |  |  |  | EV CHARGER | 1.4 |  | 0 |  |  | 0.6 | 0
[14 empty] | 1PHASE MOTOR | 2.5 |  | 0 |  |  | 0.5 | 0
23 |  |  |  |  | 0 |  |  |  | 1.25 | 0 | [9 empty] | 0.4 | 0
24 |  |  |  |  | 0 |  |  |  | 1.25 | 0 | [9 empty] | 0.3 | 0
25 |  |  |  |  | 0 |  |  |  | 1.25 | 0
26 |  |  |  |  | 0 |  |  |  | 1.25 | 0
27 |  |  |  |  | 0 |  |  |  | 1.25 | 0
28 |  |  |  |  | 0 |  |  |  | 1.25 | 0
29 |  |  |  |  | 0 |  |  |  | 1.25 | 0
30 |  |  |  |  | 0 |  |  |  | 1.25 | 0
|  | 2.46 |  |  | 10.6957 |  |  |  | 1.25 | 13.3696

## Other Computation
# OUTLETS | VA | VA | AMPERES | # OUTLETS |  | *SUBJECT TO CHANGE* | [16 empty] | KVA ASSUMPTION |  | VA/SQM |  | SQM |  | KVA
[6 empty] | FCU RATING |  |  |  |  | INTERPOLATE
1 | 180 | 0.18 | 0.78261 | 1 | [18 empty] | REGULAR OFFICE |  | 100 |  | 119.36 |  | 11.936
2 | 360 | 0.36 | 1.5652 | 2 |  | NAME | WATT | HP | AMPERES |  | X | X1 | Y1 | X2 | Y2 | Y | [6 empty] | BPO |  | 125 |  | 37.5 |  | 4.6875
3 | 540 | 0.54 | 2.3478 | 3 | [18 empty] | OFFICE + SHOWROOM |  | 125 |  | 119.36 |  | 14.92
4 | 720 | 0.72 | 3.1304 | 4 | [6 empty] | 9 | 7.5 | 14 | 10 | 18 | 16.4 | [6 empty] | LOBBY |  | 75 |  | 14.21 |  | 1.0657
5 | 900 | 0.9 | 3.913 | 5 | [18 empty] | TOILET/T&B |  | 20 |  | 4.41 |  | 0.0882
6 | 1080 | 1.08 | 4.6957 | 6 | [18 empty] | EE ROOM |  | 30 |  | 28.08 |  | 0.8424
7 | 1260 | 1.26 | 5.4783 | 7 | [18 empty] | RETAIL |  | 400 |  | 119.36 |  | 47.744
8 | 1440 | 1.44 | 6.2609 | 8 | [6 empty] | MOTOR KW TO HP | [11 empty] | KITCHEN |  | 400 |  | 7.3 |  | 2.92
9 | 1620 | 1.62 | 7.0435 | 9 | [18 empty] | RENTABLE SPACE |  | 125 |  | 235 |  | 29.375
10 | 1800 | 1.8 | 7.8261 | 10 | [6 empty] | KW |  | HP | [9 empty] | ROOFDECK |  | 20 |  | 103 |  | 2.06
11 | 1980 | 1.98 | 8.6087 | 11 | [18 empty] | PRRKING |  | 15 |  | 939.41 |  | 14.0911
12 | 2160 | 2.16 | 9.3913 | 12 | [6 empty] | 2.66 |  | 3.5657 | [9 empty] | STORAGE |  | 15 |  | 39.81 |  | 0.59715
[23 empty] | DINING AREA |  | 75 |  | 5.49 |  | 0.41175
[23 empty] | LOUNGE |  | 75 |  | 111.58 |  | 8.3685
[23 empty] | BANK |  | 100 |  |  |  | 0
[11 empty] | INCHES TO MILLIMETER |  |  |  | FEET TO METER | [7 empty] | RETAIL(DRY) |  | 250 |  | 119.36 |  | 29.84
[11 empty] | in |  | mm |  | ft |  | m
[11 empty] | 0.5 |  | 12.7 |  | 0.5 |  | 0.15239
[23 empty] | STUDIO |  | 2 |  |  |  | 0
[23 empty] | ONE BED |  | 3 |  |  |  | 0
[11 empty] | MILLIMETER TO INCHES |  |  |  | METER TO FEET | [7 empty] | 2 BED |  | 4 |  |  |  | 0
[23 empty] | 3 BED |  | 5 |  |  |  | 0
[11 empty] | mm |  | in |  | m |  | ft | [5 empty] | 4 BED |  | 6 |  |  |  | 0
[11 empty] | 25 |  | 0.98425 |  | 38 |  | 124.678
230V | 1 PHASE | [21 empty] | INTERPOLATE (1PHASE, 230V)
|  | 1/10 | 1/8 | 1/6 | 1/4 | 1/3 | 1/2 | 3/4 | 1 | 1 1/2 | [12 empty] | X | X1 | Y1 | X2 | Y2 | Y |  | AT(x2.25) | AT(x2.50)
HP |  | 0.1 | 0.125 | 0.16667 | 0.25 | 0.33333 | 0.5 | 0.75 | 1 | 1.5 | 2 | 3 | 5 | 7.5 | 10 | 15 | 20 | 25 | 30 | 40 | 50
AMPERE |  | 1.5 | 1.9 | 2.2 | 2.9 | 3.6 | 4.9 | 6.9 | 8 | 10 | 12 | 17 | 28 | 40 | 50 | 68 | 88 | 110 | 136 | 176 | 216 |  | 3.5 | 3 | 17 | 5 | 28 | 19.75 |  | 44.4375 | 49.375
230V | 3PHASE | [21 empty] | INTERPOLATE (3PHASE, 230V)
HP |  | 0.5 | 1 | 1.5 | 2 | 3 | 5 | 7.5 | 10 | 15 | 20 | 25 | 30 | 40 | 50 | 60 | 75 | 100 | 125 | 150 | 200 |  | X | X1 | Y1 | X2 | Y2 | Y |  | AT
AMPERE |  | 2.2 | 4.2 | 6 | 6.8 | 9.6 | 15.2 | 22 | 28 | 42 | 54 | 68 | 80 | 104 | 130 | 154 | 192 | 248 | 312 | 360 | 480
AT |  | 15 | 15 | 15 | 20 | 20 | 30 | 50 | 60 | 100 | 100 | 100 | 125 | 150 | 200 | 225 | 250 | 350 | 500 | 600 | 800 |  | 0.75 | 0.5 | 2.2 | 1 | 4.2 | 3.2 |  | 15
400V | 3PHASE | [21 empty] | INTERPOLATE (3PHASE, 400V)
HP |  | 0.5 | 1 | 1.5 | 2 | 3 | 5 | 7.5 | 10 | 15 | 20 | 25 | 30 | 40 | 50 | 60 | 75 | 100 | 125 | 150 | 200 |  | X | X1 | Y1 | X2 | Y2 | Y |  | AT
AMPERE |  | 1.3 | 2.3 | 3.3 | 4.3 | 6.1 | 9.7 | 14 | 18 | 27 | 34 | 44 | 51 | 66 | 83 | 103 | 128 | 165 | 208 | 240 | 320
AT |  | 15 | 15 | 20 | 20 | 20 | 20 | 30 | 40 | 60 | 70 | 100 | 100 | 100 | 125 | 150 | 200 | 250 | 300 | 350 | 500 |  | 68 | 60 | 103 | 75 | 128 | 116.3333 |  | 200
PIPE W/ LOCKNUT APPROX DIMENSION
PIPE | 15 | 20 | 25 | 32 | 50 | 65 | 80 | 90 | 100 | 110
LOCKNUT | 25 | 35 | 40 | 55 | 75 | 95 | 110 | 125 | 134 | 150
PULLBOX COMPUTATION | [8 empty] | 2ND LAYER PULLBOX COMPUTATION | [8 empty] | IF 2 LAYERS (mm) |  |  |  |  | BUSBAR AMPACITY COMPUTATION (INCHES)
Conduit Size | w/ Locknut | No. Conduit | Conduit Ref | Total Dia | Length | Width | Depth |  | Conduit Size | w/ Locknut | No. Conduit | Conduit Ref | Total Dia | Length | Width | Depth |  | Length | Width | Depth |  |  | THICKNESS | WIDTH | PLY | AMPACITY
15 | 25 | 0 | 0 | 0 |  |  | 0 |  | 15 | 25 | 0 | 0 | 0 |  |  | 0
20 | 35 | 0 | 0 | 0 |  |  | 0 |  | 20 | 35 | 0 | 0 | 0 |  |  | 0 |  | 0 | 0 | 0 |  |  | 0.25 | 2 | 1 | 500
25 | 40 | 0 | 0 | 0 |  |  | 0 |  | 25 | 40 | 0 | 0 | 0 |  |  | 0
32 | 55 | 0 | 0 | 0 |  |  | 0 |  | 32 | 55 | 0 | 0 | 0 |  |  | 0 |  | INCHES
50 | 75 | 0 | 0 | 0 |  |  | 0 |  | 50 | 75 | 0 | 0 | 0 |  |  | 0 | [6 empty] | BUSBAR AMPACITY COMPUTATION (mm)
65 | 90 | 0 | 0 | 0 |  |  | 0 |  | 65 | 90 | 0 | 0 | 0 |  |  | 0 |  | 0 | 0 | 0
80 | 110 | 0 | 0 | 0 |  |  | 0 |  | 80 | 110 | 0 | 0 | 0 |  |  | 0 | [6 empty] | THICKNESS | WIDTH | PLY | AMPACITY
90 | 120 | 0 | 0 | 0 |  |  | 0 |  | 90 | 120 | 0 | 0 | 0 |  |  | 0
100 | 135 | 0 | 0 | 0 |  |  | 0 |  | 100 | 135 | 0 | 0 | 0 |  |  | 0 | [6 empty] | 3.175 | 12.7 | 1 | 62.4999
110 | 150 | 0 | 0 | 0 |  |  | 0 |  | 110 | 150
|  | 0 |  |  | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 | 0 | 0
[5 empty] | INCHES | [8 empty] | INCHES
[5 empty] | 0 | 0 | 0 | [6 empty] | 0 | 0 | 0
CABLE TRAY COMPUTATION | [8 empty] | PERCENT FILL COMPUTATION | [7 empty] | Circle |  |  | AWG to mm²
CONDUIT
FIRE-RATED CABLE | [8 empty] | Wires |  |  | Conduit |  |  |  |  | Area | Diameter |  | AWG | mm² | mm dia
Single Core | [8 empty] | Wire Dia | # of Wires | Area | Diameter | Area | %Fill |  |  | 100 | 11.2838 |  |  | - | -
Size (sq.mm) | Approx Dia. | No. of Sets | Diameter | CHECK | Width | Depth
50 | 14.8 | 0 | - | 0 |  |  |  |  | 27.9 | 6 | 3668.1707 | 110 | 9503.3178 | 38.5988 | PASS
70 | 17 | 0 | - | 0
95 | 18.7 | 0 | - | 0 |  |  |  |  | MINIMUM PERCENT FILL
120 | 20.6 | 0 | - | 0 |  |  |  |  | 1 | WIRE |  | 53
150 | 23.1 | 0 | - | 0 |  |  |  |  | 2 | WIRES |  | 31
185 | 25.2 | 0 | - | 0 |  |  |  |  | 3 | OR MORE |  | 40
240 | 27.9 | 3 | 27.9 | 1
|  | 3 | 27.9 | 27.9 | 407.34 | 150
PERCENT FILL COMPUTATION
CABLE TRAY
Wires
Wire Dia | # of Wires | Ground Dia | Area | Width | Height | Area | %Fill | Status
27.9 | 16 |  | 9781.7885 | 300 | 150 | 45000 | 21.7373 | FAIL

## Wiring Code
LOAD SCHEDULE WIRING CODE
AT | CODE | FEEDER WIRES AND CONDUIT SIZE | CONDUIT (mmØ)
1 PHASE: 2-WIRE + GROUND |  |  | IMC/EMT | PVC | SIZE |  | OUTSIDE DIAMETER (mm) |  |  | INSIDE DIAMETER (mm)
20 | W0 | 3#2.0 mmØ THHN/THWN in 15mmØ INSIDE DIAMETER CONDUIT |  |  | mm | in | PVC SCH 40 | IMC | EMT | PVC SCH 40 | IMC | EMT
30 | W1 | 2#5.5 sq.mm THHN/THWN and 1#2.0 mmØ THNN/THWN in 20mmØ INSIDE DIAMETER CONDUIT |  |  | 15 | 0.5 | 21.336 | 20.7 | 17.93 | 15.2908 | 17.12 | 15.89
40 | W2 | 2#8.0 sq.mm THHM/THWN and 1#5.5 sq.mm THNN/THWN in 20mmØ INSIDE DIAMETER CONDUIT |  |  | 20 | 0.75 | 26.67 | 26.14 | 23.42 | 20.4216 | 22.34 | 21.06
50/60 | W3 | 2#14 sq.mm THHN/THWN and 1#8.0 sq.mm THHN/THWN in 25mmØ INSIDE DIAMETER CONDUIT |  |  | 25 | 1 | 33.401 | 33.27 | 29.54 | 26.1366 | 28.95 | 26.8
70/80 | W4 | 2#22 sq.mm THHN/THWN and 1#8.0 sq.mm THHN/THWN in 32mmØ INSIDE DIAMETER CONDUIT |  |  | 32 | 1.25 | 42.164 | 41.59 | 38.35 | 34.544 | 37.01 | 35.21
100 | W5 | 2#30 sq.mm THHN/THWN and 1#8.0 sq.mm THNN/THWN in 32mmØ INSIDE DIAMETER CONDUIT |  |  | 40 | 1.5 | 48.26 | 47.81 | 44.2 | 40.386 | 42.99 | 41.06
125 | W6 | 2#50 sq.mm THHN/THWN and 1#14 sq.mm THNN/THWN in 50mmØ INSIDE DIAMETER CONDUIT |  |  | 50 | 2 | 60.325 | 59.93 | 55.8 | 51.9938 | 52.81 | 52.66
150 | W7 | 2#60 sq.mm THHN/THWN and 1#22 sq.mm THNN/THWN in 50mmØ INSIDE DIAMETER CONDUIT |  |  | 65 | 2.5 | 73.025 | 72.56 | - | 62.103 | 65.44 | -
200 | W8 | 2#80 sq.mm THHN/THWN and 1#22 sq.mm THNN/THWN in 50mmØ INSIDE DIAMETER CONDUIT |  |  | 80 | 3 | 88.9 | 88.29 | - | 77.2668 | 81.17 | -
225 | W9 | 2#100 sq.mm THHN/THWN and 1#30 sq.mm THNN/THWN in 65mmØ INSIDE DIAMETER CONDUIT |  |  | 90 | 3.5 | 101.6 | 100.86 | - | 89.4334 | 93.74 | -
250 | W10 | 2#125sq.mm THHN/THWN and 1#30 sq.mm THNN/THWN in 65mmØ INSIDE DIAMETER CONDUIT |  |  | 100 | 4 | 114.3 | 113.4 | - | 101.5492 | 106.28 | -
275 | W11 | 2#150 sq.mm THHN/THWN and 1#30 sq.mm THNN/THWN in 80mmØ INSIDE DIAMETER CONDUIT
300 | W12 | 2#200 sq.mm THHN/THWN and 1#30 sq.mm THNN/THWN in 80mmØ INSIDE DIAMETER CONDUIT
400 | W13 | 2#250 sq.mm THHN/THWN and 1#50 sq.mm THNN/THWN in 90mmØ INSIDE DIAMETER CONDUIT
3 PHASE: 3-WIRE + GROUND : FOR ACCU, EF, PUMP, JF |  |  | IMC/EMT | PVC | PERCENT FILL COMPUTATION
20 | X0 | 4#2.0 mmØ THHN/THWN in 15mmØ INSIDE DIAMETER CONDUIT |  |  | CONDUIT
30 | X1 | 3#5.5 sq.mm THHN/THWN and 1#2.0 mmØ THNN/THWN in 20mmØ INSIDE DIAMETER CONDUIT |  |  | Wires |  |  | Conduit
40 | X2 | 3#8.0 sq.mm THHN/THWN and 1#5.5 sq.mm THNN/THWN in 25mmØ INSIDE DIAMETER CONDUIT |  |  | Wire Dia | # of Wires | Area | Diameter | Area | %Fill
50/60 | X3 | 3#14 sq.mm THHN/THWN and 1#8.0 sq.mm THNN/THWN in 25mmØ INSIDE DIAMETER CONDUIT
70/80 | X4 | 3#22 sq.mm THHN/THWN and 1#8.0 sq.mm THNN/THWN in 32mmØ INSIDE DIAMETER CONDUIT |  |  | 3 | 10 | 70.6858 | 15 | 176.7146 | 40 | PASS
100 | X5 | 3#30 sq.mm THHN/THWN and 1#8.0 sq.mm THNN/THWN in 32mmØ INSIDE DIAMETER CONDUIT
125 | X6 | 3#50 sq.mm THHN/THWN and 1#14 sq.mm THNN/THWN in 50mmØ INSIDE DIAMETER CONDUIT |  |  | MINIMUM PERCENT FILL
150 | X7 | 3#60 sq.mm THHN/THWN and 1#22 sq.mm THNN/THWN in 50mmØ INSIDE DIAMETER CONDUIT |  |  | 1 | WIRE |  | 53
200 | X8 | 3#80 sq.mm THHN/THWN and 1#22 sq.mm THNN/THWN in 50mmØ INSIDE DIAMETER CONDUIT |  |  | 2 | WIRES |  | 31
225 | X9 | 3#100 sq.mm THHN/THWN and 1#30 sq.mm THNN/THWN in 65mmØ INSIDE DIAMETER CONDUIT |  |  | 3 | OR MORE |  | 40
250 | X10 | 3#125sq.mm THHN/THWN and 1#30 sq.mm THNN/THWN in 65mmØ INSIDE DIAMETER CONDUIT
275 | X11 | 3#150 sq.mm THHN/THWN and 1#30 sq.mm THNN/THWN in 80mmØ INSIDE DIAMETER CONDUIT
300 | X12 | 3#200 sq.mm THHN/THWN and 1#30 sq.mm THNN/THWN in 80mmØ INSIDE DIAMETER CONDUIT
400 | X13 | 3#250 sq.mm THHN/THWN and 1#50 sq.mm THNN/THWN in 90mmØ INSIDE DIAMETER CONDUIT |  |  | PERCENT FILL COMPUTATION
CABLE TRAY
3 PHASE: 3-WIRE + NEUTRAL + GROUND : FOR MAINS |  |  | IMC/EMT | PVC | Wires
20 | Y0 | 5#2.0 mmØ THHN/THWN in 15mmØ INSIDE DIAMETER CONDUIT |  |  | Wire Dia | # of Wires | Ground Dia | Area | Width | Height | Area | %Fill | Status
30 | Y1 | 4#5.5 sq.mm THHM/THWN and 1#2.0 mmØ THNN/THWN in 20mmØ INSIDE DIAMETER CONDUIT
40 | Y2 | 4#8.0 sq.mm THHM/THWN and 1#5.5 sq.mm THNN/THWN in 25mmØ INSIDE DIAMETER CONDUIT |  |  | 27.9 | 16 |  | 9781.7885 | 400 | 150 | 60000 | 16.303 | PASS
50/60 | Y3 | 4#14 sq.mm THHM/THWN and 1#8.0 sq.mm THNN/THWN in 25mmØ INSIDE DIAMETER CONDUIT
70/80 | Y4 | 4#22 sq.mm THHM/THWN and 1#8.0 sq.mm THNN/THWN in 32mmØ INSIDE DIAMETER CONDUIT
100 | Y5 | 4#30 sq.mm THHM/THWN and 1#8.0 sq.mm THNN/THWN in 32mmØ INSIDE DIAMETER CONDUIT |  |  | WXY-0 | 15mmØ INSIDE DIAMETER CONDUIT
125 | Y6 | 4#50 sq.mm THHM/THWN and 1#14 sq.mm THNN/THWN in 50mmØ INSIDE DIAMETER CONDUIT |  |  | WXY-1 | 20mmØ INSIDE DIAMETER CONDUIT
150 | Y7 | 4#60 sq.mm THHM/THWN and 1#22 sq.mm THNN/THWN in 50mmØ INSIDE DIAMETER CONDUIT |  |  | WXY-2 | 20mmØ INSIDE DIAMETER CONDUIT
200 | Y8 | 4#80 sq.mm THHM/THWN and 1#22 sq.mm THNN/THWN in 50mmØ INSIDE DIAMETER CONDUIT |  |  | WXY-3 | 25mmØ INSIDE DIAMETER CONDUIT
225 | Y9 | 4#100 sq.mm THHM/THWN and 1#30 sq.mm THNN/THWN in 65mmØ INSIDE DIAMETER CONDUIT |  |  | WXY-4 | 32mmØ INSIDE DIAMETER CONDUIT
250 | Y10 | 4#125sq.mm THHM/THWN and 1#30 sq.mm THNN/THWN in 65mmØ INSIDE DIAMETER CONDUIT |  |  | WXY-5 | 32mmØ INSIDE DIAMETER CONDUIT
275 | Y11 | 4#150 sq.mm THHM/THWN and 1#30 sq.mm THNN/THWN in 80mmØ INSIDE DIAMETER CONDUIT |  |  | WXY-6 | 50mmØ INSIDE DIAMETER CONDUIT
300 | Y12 | 4#200 sq.mm THHM/THWN and 1#30 sq.mm THNN/THWN in 80mmØ INSIDE DIAMETER CONDUIT |  |  | WXY-7 | 50mmØ INSIDE DIAMETER CONDUIT
400 | Y13 | 4#250 sq.mm THHM/THWN and 1#50 sq.mm THNN/THWN in 90mmØ INSIDE DIAMETER CONDUIT |  |  | WXY-8 | 50mmØ INSIDE DIAMETER CONDUIT
[5 empty] | WXY-9 | 65mmØ INSIDE DIAMETER CONDUIT
3 PHASE (FIRE-RATED OHLS): 3-WIRE + GROUND : FOR FIRE-LIFE SAFETY LOADS |  |  | IMC/EMT | PVC | WXY-10 | 65mmØ INSIDE DIAMETER CONDUIT
20 | ZX0 | 4#2.0 mmØ 3-HOURS FIRE-RATED CU/MICA/XLPE/LSOH CABLES in 25mmØ INSIDE DIAMETER CONDUIT |  |  | WXY-11 | 80mmØ INSIDE DIAMETER CONDUIT
30 | ZX1 | 3#5.5 sq.mm 3-HOURS FIRE-RATED CU/MICA/XLPE/LSOH CABLES and 1#2.0 mmØ THNN/THWN in 25mmØ ID CONDUIT |  |  | WXY-12 | 80mmØ INSIDE DIAMETER CONDUIT
40 | ZX2 | 3#8.0 sq.mm 3-HOURS FIRE-RATED CU/MICA/XLPE/LSOH CABLES and 1#5.5 sq.mm THNN/THWN in 25mmØ ID CONDUIT |  |  | WXY-13 | 90mmØ INSIDE DIAMETER CONDUIT
50/60 | ZX3 | 3#14 sq.mm 3-HOURS FIRE-RATED CU/MICA/XLPE/LSOH CABLES and 1#8.0 sq.mm THNN/THWN in 25mmØ ID CONDUIT
70/80 | ZX4 | 3#22 sq.mm 3-HOURS FIRE-RATED CU/MICA/XLPE/LSOH CABLES and 1#8.0 sq.mm THNN/THWN in 32mmØ ID CONDUIT
100 | ZX5 | 3#30 sq.mm 3-HOURS FIRE-RATED CU/MICA/XLPE/LSOH CABLES and 1#8.0 sq.mm THNN/THWN in 50mmØ ID CONDUIT
125 | ZX6 | 3#50 sq.mm 3-HOURS FIRE-RATED CU/MICA/XLPE/LSOH CABLES and 1#14 sq.mm THNN/THWN in 50mmØ ID CONDUIT
150 | ZX7 | 3#60 sq.mm 3-HOURS FIRE-RATED CU/MICA/XLPE/LSOH CABLES and 1#22 sq.mm THNN/THWN in 50mmØ ID CONDUIT
200 | ZX8 | 3#80 sq.mm 3-HOURS FIRE-RATED CU/MICA/XLPE/LSOH CABLES and 1#22 sq.mm THNN/THWN in 50mmØ ID CONDUIT
225 | ZX9 | 3#100 sq.mm 3-HOURS FIRE-RATED CU/MICA/XLPE/LSOH CABLES and 1#30 sq.mm THNN/THWN in CABLE TRAY
250 | ZX10 | 3#125sq.mm 3-HOURS FIRE-RATED CU/MICA/XLPE/LSOH CABLES and 1#30 sq.mm THNN/THWN in CABLE TRAY
275 | ZX11 | 3#150 sq.mm 3-HOURS FIRE-RATED CU/MICA/XLPE/LSOH CABLES and 1#30 sq.mm THNN/THWN in CABLE TRAY
300 | ZX12 | 3#200 sq.mm 3-HOURS FIRE-RATED CU/MICA/XLPE/LSOH CABLES and 1#30 sq.mm THNN/THWN in CABLE TRAY
400 | ZX13 | 3#250 sq.mm 3-HOURS FIRE-RATED CU/MICA/XLPE/LSOH CABLES and 1#50 sq.mm THNN/THWN in CABLE TRAY
3 PHASE (FIRE-RATED OHLS): 3-WIRE + NEUTRAL + GROUND : FOR FIRE-LIFE SAFETY LOADS |  |  | IMC/EMT | PVC
20 | ZY0 | 5#2.0 mmØ 3-HOURS FIRE-RATED CU/MICA/XLPE/LSOH CABLES in 25mmØ INSIDE DIAMETER CONDUIT
30 | ZY1 | 4#5.5 sq.mm 3-HOURS FIRE-RATED CU/MICA/XLPE/LSOH CABLES and 1#5.5 sq.mm THNN/THWN in 32mmØ ID CONDUIT
40 | ZY2 | 4#8.0 sq.mm 3-HOURS FIRE-RATED CU/MICA/XLPE/LSOH CABLES and 1#5.5 sq.mm THNN/THWN in 32mmØ ID CONDUIT
50/60 | ZY3 | 4#14 sq.mm 3-HOURS FIRE-RATED CU/MICA/XLPE/LSOH CABLES and 1#8.0 sq.mm THNN/THWN in 32mmØ ID CONDUIT
70/80 | ZY4 | 4#22 sq.mm 3-HOURS FIRE-RATED CU/MICA/XLPE/LSOH CABLES and 1#8.0 sq.mm THNN/THWN in 32mmØ ID CONDUIT
100 | ZY5 | 4#30 sq.mm 3-HOURS FIRE-RATED CU/MICA/XLPE/LSOH CABLES and 1#8.0 sq.mm THNN/THWN in 50mmØ ID CONDUIT
125 | ZY6 | 4#50 sq.mm 3-HOURS FIRE-RATED CU/MICA/XLPE/LSOH CABLES and 1#14 sq.mm THNN/THWN in 50mmØ ID CONDUIT
150 | ZY7 | 4#60 sq.mm 3-HOURS FIRE-RATED CU/MICA/XLPE/LSOH CABLES and 1#22 sq.mm THNN/THWN in 50mmØ ID CONDUIT
200 | ZY8 | 4#80 sq.mm 3-HOURS FIRE-RATED CU/MICA/XLPE/LSOH CABLES and 1#22 sq.mm THNN/THWN in 50mmØ ID CONDUIT
225 | ZY9 | 4#100 sq.mm 3-HOURS FIRE-RATED CU/MICA/XLPE/LSOH CABLES and 1#30 sq.mm THNN/THWN in CABLE TRAY
250 | ZY10 | 4#125sq.mm 3-HOURS FIRE-RATED CU/MICA/XLPE/LSOH CABLES and 1#30 sq.mm THNN/THWN in CABLE TRAY
275 | ZY11 | 4#150 sq.mm 3-HOURS FIRE-RATED CU/MICA/XLPE/LSOH CABLES and 1#30 sq.mm THNN/THWN in CABLE TRAY
300 | ZY12 | 4#200 sq.mm 3-HOURS FIRE-RATED CU/MICA/XLPE/LSOH CABLES and 1#30 sq.mm THNN/THWN in CABLE TRAY
400 | ZY13 | 4#250 sq.mm 3-HOURS FIRE-RATED CU/MICA/XLPE/LSOH CABLES and 1#50 sq.mm THNN/THWN in CABLE TRAY
3 PHASE (ALUMINUM): 3-WIRE + GROUND : MAINS (SIZE≈2×DIA. OF COPPER) |  |  | IMC/EMT | PVC
125 | AX9 | 3#100sq.mm THHN/THWN and 1#30 sq.mm THHN/THWN in 80mm INSIDE Ø CONDUIT | 80mmØ (INSIDE DIAMETER)
150 | AX10 | 3#125sq.mm THHN/THWN and 1#50 sq.mm THHN/THWN in 80mm INSIDE Ø CONDUIT | 80mmØ (INSIDE DIAMETER)
175 | AX11 | 3#150sq.mm THHN/THWN and 1#50 sq.mm THHN/THWN in 90mm INSIDE Ø CONDUIT | 90mmØ (INSIDE DIAMETER)
200 | AX12 | 3#200sq.mm THHN/THWN and 1#60 sq.mm THHN/THWN in 100mm INSIDE Ø CONDUIT | 100mmØ (INSIDE DIAMETER)
250 | AX13 | 3#250sq.mm THHN/THWN and 1#80 sq.mm THHN/THWN in 100mm INSIDE Ø CONDUIT | 100mmØ (INSIDE DIAMETER)
300 | AX14 | 3#325sq.mm THHN/THWN and 1#100 sq.mm THHN/THWN in 100mm INSIDE Ø CONDUIT | 100mmØ (INSIDE DIAMETER)
400 | 2AX12 | 2 SETS (3#125sq.mm THHN/THWN and 1#30 sq.mm THHN/THWN in 100mm INSIDE Ø CONDUIT) | 2-100mmØ (INSIDE DIAMETER)
600 | 2AX14 | 3 SETS (3#125sq.mm THHN/THWN and 1#30 sq.mm THHN/THWN in 100mm INSIDE Ø CONDUIT) | 2-100mmØ (INSIDE DIAMETER)
3 PHASE (ALUMINUM): 3-WIRE + NEUTRAL + GROUND : MAINS (SIZE≈2×DIA. OF COPPER) |  |  | IMC/EMT | PVC
125 | AY9 | 4#100sq.mm THHN/THWN and 1#30 sq.mm THHN/THWN in 80mm INSIDE Ø CONDUIT | 80mmØ (INSIDE DIAMETER)
150 | AY10 | 4#125sq.mm THHN/THWN and 1#50 sq.mm THHN/THWN in 80mm INSIDE Ø CONDUIT | 80mmØ (INSIDE DIAMETER)
175 | AY11 | 4#150sq.mm THHN/THWN and 1#50 sq.mm THHN/THWN in 90mm INSIDE Ø CONDUIT | 90mmØ (INSIDE DIAMETER)
200 | AY12 | 4#200sq.mm THHN/THWN and 1#60 sq.mm THHN/THWN in 100mm INSIDE Ø CONDUIT | 100mmØ (INSIDE DIAMETER)
250 | AY13 | 4#250sq.mm THHN/THWN and 1#80 sq.mm THHN/THWN in 100mm INSIDE Ø CONDUIT | 100mmØ (INSIDE DIAMETER)
300 | AY14 | 4#325sq.mm THHN/THWN and 1#100 sq.mm THHN/THWN in 100mm INSIDE Ø CONDUIT | 100mmØ (INSIDE DIAMETER)
400 | 2AY12 | 2 SETS (4#125sq.mm THHN/THWN and 1#30 sq.mm THHN/THWN in 100mm INSIDE Ø CONDUIT) | 2-100mmØ (INSIDE DIAMETER)
600 | 2AY13 | 2 SETS (4#125sq.mm THHN/THWN and 1#30 sq.mm THHN/THWN in 100mm INSIDE Ø CONDUIT) | 2-100mmØ (INSIDE DIAMETER)
1 PHASE (BRANCH CABLE): 2-WIRE + GROUND
70 | BC-W1 | 2#10 sq.mm Cu PRE-FABRICATED BRANCH CABLE SYSTEM and 1#8.0 sq.mm THHN/THWN GROUND
80 | BC-W2 | 2#16 sq.mm Cu PRE-FABRICATED BRANCH CABLE SYSTEM and 1#8.0 sq.mm THHN/THWN GROUND
125 | BC-W3 | 2#25 sq.mm Cu PRE-FABRICATED BRANCH CABLE SYSTEM and 1#8.0 sq.mm THHN/THWN GROUND
150 | BC-W4 | 2#35 sq.mm Cu PRE-FABRICATED BRANCH CABLE SYSTEM and 1#14.0 sq.mm THHN/THWN GROUND
200 | BC-W5 | 2#50 sq.mm Cu PRE-FABRICATED BRANCH CABLE SYSTEM and 1#14.0 sq.mm THHN/THWN GROUND
250 | BC-W6 | 2#70 sq.mm Cu PRE-FABRICATED BRANCH CABLE SYSTEM and 1#22.0 sq.mm THHN/THWN GROUND
300 | BC-W7 | 2#95 sq.mm Cu PRE-FABRICATED BRANCH CABLE SYSTEM and 1#30.0 sq.mm THHN/THWN GROUND
350 | BC-W8 | 2#120 sq.mm Cu PRE-FABRICATED BRANCH CABLE SYSTEM and 1#30.0 sq.mm THHN/THWN GROUND
400 | BC-W9 | 2#150 sq.mm Cu PRE-FABRICATED BRANCH CABLE SYSTEM and 1#30.0 sq.mm THHN/THWN GROUND
500 | BC-W10 | 2#186 sq.mm Cu PRE-FABRICATED BRANCH CABLE SYSTEM and 1#30.0 sq.mm THHN/THWN GROUND
3 PHASE (BRANCH CABLE): 3-WIRE + NEUTRAL + GROUND
70 | BC-Y1 | 2#10 sq.mm Cu PRE-FABRICATED BRANCH CABLE SYSTEM and 1#8.0 sq.mm THHN/THWN GROUND
80 | BC-Y2 | 2#16 sq.mm Cu PRE-FABRICATED BRANCH CABLE SYSTEM and 1#8.0 sq.mm THHN/THWN GROUND
125 | BC-Y3 | 2#25 sq.mm Cu PRE-FABRICATED BRANCH CABLE SYSTEM and 1#8.0 sq.mm THHN/THWN GROUND
150 | BC-Y4 | 2#35 sq.mm Cu PRE-FABRICATED BRANCH CABLE SYSTEM and 1#14.0 sq.mm THHN/THWN GROUND
200 | BC-Y5 | 2#50 sq.mm Cu PRE-FABRICATED BRANCH CABLE SYSTEM and 1#14.0 sq.mm THHN/THWN GROUND
250 | BC-Y6 | 2#70 sq.mm Cu PRE-FABRICATED BRANCH CABLE SYSTEM and 1#22.0 sq.mm THHN/THWN GROUND
300 | BC-Y7 | 2#95 sq.mm Cu PRE-FABRICATED BRANCH CABLE SYSTEM and 1#30.0 sq.mm THHN/THWN GROUND
350 | BC-Y8 | 2#120 sq.mm Cu PRE-FABRICATED BRANCH CABLE SYSTEM and 1#30.0 sq.mm THHN/THWN GROUND
400 | BC-Y9 | 2#150 sq.mm Cu PRE-FABRICATED BRANCH CABLE SYSTEM and 1#30.0 sq.mm THHN/THWN GROUND
500 | BC-Y10 | 2#186 sq.mm Cu PRE-FABRICATED BRANCH CABLE SYSTEM and 1#30.0 sq.mm THHN/THWN GROUND

## Voltage Drop
Voltage Drop (Vd) = kDI x √(R²+X²) / n | [7 empty] | Phase | k |  | Total VD | 6.2581
Voltage Drop (Vd) = kDI x [R*cos(Ө)+X*sin(Ө)] / n | [7 empty] | 1 | 2 |  | Total % VD | 2.721%
[8 empty] | 3 | 1.732
k = Constant (2 for single phase, 1.732 for three phase
D = Distance or Length of the conductor (m) | [7 empty] | Conduit Type
I = Current in Amperes | [7 empty] | PVC
R = Line AC Resistance per 305m | [7 empty] | Metal
X = Line AC Reactance per 305m
Ө = cos(pf)
pf = Power Factor, Assumed 85%
n = Number of wire per phase or the number of sets
VD Number | Phase | Column1 | k | D | I | n | Wire Code | Conductor Type | Wire Dia (mm²) | Conduit | R | X | Voltage Drop | %VD
1 | 3 | 230 | 1.732 | 8 | 200 | 1 | X8 | CU | 80 | Metal | 0.079 | 0.052 | 0.86053 | 0.3741%
2 | 1 | 230 | 2 | 49.16 | 16 | 1 | W1 | CU | 5.5 | PVC | 1.2 | 0.05 | 5.3976 | 2.347%
3 |  |  | - |  |  |  |  | - | - |  | - | - | - | -
4 |  |  | - |  |  |  |  | - | - |  | - | - | - | -
5 |  |  | - |  |  |  |  | - | - |  | - | - | - | -
6 |  |  | - |  |  |  |  | - | - |  | - | - | - | -
7 |  |  | - |  |  |  |  | - | - |  | - | - | - | -
8 |  |  | - |  |  |  |  | - | - |  | - | - | - | -
9 |  |  | - |  |  |  |  | - | - |  | - | - | - | -
10 |  |  | - |  |  |  |  | - | - |  | - | - | - | -
11 |  |  | - |  |  |  |  | - | - |  | - | - | - | -
12 |  |  | - |  |  |  |  | - | - |  | - | - | - | -
13 |  |  | - |  |  |  |  | - | - |  | - | - | - | -
14 |  |  | - |  |  |  |  | - | - |  | - | - | - | -
15 |  |  | - |  |  |  |  | - | - |  | - | - | - | -
16 |  |  | - |  |  |  |  | - | - |  | - | - | - | -
17 |  |  | - |  |  |  |  | - | - |  | - | - | - | -
18 |  |  | - |  |  |  |  | - | - |  | - | - | - | -
19 |  |  | - |  |  |  |  | - | - |  | - | - | - | -
20 |  |  | - |  |  |  |  | - | - |  | - | - | - | -
21 |  |  | - |  |  |  |  | - | - |  | - | - | - | -
22 |  |  | - |  |  |  |  | - | - |  | - | - | - | -
23 |  |  | - |  |  |  |  | - | - |  | - | - | - | -
24 |  |  | - |  |  |  |  | - | - |  | - | - | - | -
25 |  |  | - |  |  |  |  | - | - |  | - | - | - | -

## Short Circuit Analysis
Short Circuit Calculation
Phase
IFL (3 Phase) = VA/(V*1.732) | [8 empty] | V Factor | k | [5 empty] | METER | FEET
IFL (1 Phase) = VA/V | [7 empty] | 3 | 1.732 | 1.732
M (Transformer) = 100/(Transformer %Z) | [7 empty] | 1 | 1 | 2 | [5 empty] | 18.12 | 59.4488
I(SC) = IFL * M
f = (k*L*I)/C*n*V
M = 1/(1 + f) | [15 empty] | FEET | METER
IFL: Full Load Ampere | [15 empty] | 95.14 | 28.9987
f: Factor at Fault Point | [7 empty] | NOTE:
k: 1.732 (3-Phase), 2 (Single Phase) | [7 empty] | 3SC = 3 Single Conductors
M: Multiplier at point f | [7 empty] | 3CC = 3 Conductor Cable
I(SC): Available Short-Circuit Current at Beginning of Circuit | [7 empty] | PVC = Nonmagnetic
L: Length (ft) of Conductor to the Fault | [7 empty] | Stl = Steel
C: Constant from Conductor
n: Number of Conductors per Phase
V: Voltage
Reference: Point-to-Point Calculation Procedure from Short Circtui Calculations, Bussmann by Eaton
Fault (Xformer) | KVA | V | Phase | IFL | %Z | M | I(SC)
0 | 75 | 230 | 3 | 188.2719 | 1.1 | 90.9091 | 17115.6286
Fault # | Phase | k | L | Ref Fault # | I(SC) Old | Wire Code | Con Dia / Amp | Conductor Type | Conductor Type2 | Conduit Type | Cable Rating | C | n | V | f | M | I(SC) New | NOTES
1 | 3 | 1.732 | 26.2467 |  | 17115.6286 | X8 | 80 | CU | 3SC | Stl | 600V | 12844 | 1 | 230 | 0.26338 | 0.79153 | 13547.459 | Transformer to Main Panel
2 | 1 | 2 | 59.4488 | 1 | 13547.459 | W4 | 22 | CU | 3SC | PVC | 600V | 3826 | 1 | 230 | 1.8305 | 0.3533 | 4786.325 | Main Panel to PB-2
3 | 1 | 2 | 5.9056 | 2 | 4786.325 | W0 | 3.5 | CU | 3SC | PVC | 600V | 617 | 1 | 230 | 0.39837 | 0.71512 | 3422.7964 | pb-2 to nearest outlet
4 | 1 | 2 | 78.74 | 1 | 13547.459 | W3 | 14 | CU | 3SC | PVC | 600V | 2430 | 1 | 230 | 3.8172 | 0.20759 | 2812.2882 | main to pb-1
5 | 1 | 2 | 7 | 4 | 2812.2882 | W0 | 3.5 | CU | 3SC | PVC | 600V | 617 | 1 | 230 | 0.27744 | 0.78281 | 2201.4968 | pb-1 to nearest outlet
6 | 1 | 2 | 95.14 | 1 | 13547.459 | W0 | 3.5 | CU | 3SC | PVC | 600V | 617 | 1 | 230 | 18.1651 | 0.052178 | 706.8814
7 |  | - |  |  | - |  | - | - |  |  |  | - |  |  | - | - | -
8 |  | - |  |  | - |  | - | - |  |  |  | - |  |  | - | - | -
9 |  | - |  |  | - |  | - | - |  |  |  | - |  |  | - | - | -
10 |  | - |  |  | - |  | - | - |  |  |  | - |  |  | - | - | -
12 |  | - |  |  | - |  | - | - |  |  |  | - |  |  | - | - | -
13 |  | - |  |  | - |  | - | - |  |  |  | - |  |  | - | - | -
14 |  | - |  |  | - |  | - | - |  |  |  | - |  |  | - | - | -
15 |  | - |  |  | - |  | - | - |  |  |  | - |  |  | - | - | -
16 |  | - |  |  | - |  | - | - |  |  |  | - |  |  | - | - | -
17 |  | - |  |  | - |  | - | - |  |  |  | - |  |  | - | - | -
18 |  | - |  |  | - |  | - | - |  |  |  | - |  |  | - | - | -
19 |  | - |  |  | - |  | - | - |  |  |  | - |  |  | - | - | -
20 |  | - |  |  | - |  | - | - |  |  |  | - |  |  | - | - | -
21 |  | - |  |  | - |  | - | - |  |  |  | - |  |  | - | - | -
22 |  | - |  |  | - |  | - | - |  |  |  | - |  |  | - | - | -
23 |  | - |  |  | - |  | - | - |  |  |  | - |  |  | - | - | -
24 |  | - |  |  | - |  | - | - |  |  |  | - |  |  | - | - | -
25 |  | - |  |  | - |  | - | - |  |  |  | - |  |  | - | - | -

## Table Reference
AC Resistance and Reactance for 600V Cables, 3-Phase, 60Hz, 75°C - Three (3) Single Conductors in Conduit PEC 2017 TABLE 10.1.1.9 | [9 empty] | LOAD SCHEDULE WIRING CODE | [16 empty] | Table 4. “C” Values for Conductors
[10 empty] | AT | CODE | SETS | WIRE# | WIRE DIA | UNIT | TYPE | GRND DIA | UNIT | TYPE | RACEWAY | RACEWAY REF | [5 empty] | Copper | [13 empty] | Aluminum
Conductor Size |  | Ohms to Neutral per 305m | [26 empty] | Three Single Conductors | [5 empty] | Three-Conductor Cable | [7 empty] | Three Single Conductors | [5 empty] | Three-Conductor Cable
|  | XL (Reactance) |  | AC Resitance -Cu |  |  | AC Resistance-AL |  |  | 1 PHASE: 2-WIRE + GROUND | [11 empty] | WIRE CODE | CODE | TYPE | CODE | WIRE CORE SIZE |  |  | Conduit | [5 empty] | Conduit | [7 empty] | Conduit | [5 empty] | Conduit
[mm²] | (mm dia.) | PVC | Steel | PVC | Al | Steel | PVC | Al | Steel | 20 | W0 |  | 2 | 2 | mmØ | THHN/THWN | 2 | mmØ | THHN/THWN | 15mmØ | INSIDE DIAMETER | W0 | 1 | CU | 0 | 2 | mm² | AWG or kcmil | Steel |  |  | Nonmagnetic |  |  | Steel |  |  | Nonmagnetic |  |  | mm² | AWG or kcmil | Steel |  |  | Nonmagnetic |  |  | Steel |  |  | Nonmagnetic
2 | 1.6 | 0.058 | 0.073 | 3.1 | 3.1 | 3.1 | - | - | - | 30 | W1 |  | 2 | 5.5 | sq.mm | THHN/THWN | 2 | mmØ | THNN/THWN | 20mmØ | INSIDE DIAMETER | W1 | 2 | CU | 1 | 3.5 |  |  | 600V | 5kV | 15kV | 600V | 5kV | 15kV | 600V | 5kV | 15kV | 600V | 5kV | 15kV |  |  | 600V | 5kV | 15kV | 600V | 5kV | 15kV | 600V | 5kV | 15kV | 600V | 5kV | 15kV
3.5 | 2 | 0.054 | 0.068 | 2 | 2 | 2 | 3.2 | 3.2 | 3.2 | 40 | W2 |  | 2 | 8 | sq.mm | THHM/THWN | 5.5 | sq.mm | THNN/THWN | 20mmØ | INSIDE DIAMETER | W2 | 3 | CU | 2 | 5.5 |  |  | CU3SCStl600V | CU3SCStl5kV | CU3SCStl15kV | CU3SCPVC600V | CU3SCPVC5kV | CU3SCPVC15kV | CU3CCStl600V | CU3CCStl5kV | CU3CCStl15kV | CU3CCPVC600V | CU3CCPVC5kV | CU3CCPVC15kV |  |  | AL3SCStl600V | AL3SCStl5kV | AL3SCStl15kV | AL3SCPVC600V | AL3SCPVC5kV | AL3SCPVC15kV | AL3CCStl600V | AL3CCStl5kV | AL3CCStl15kV | AL3CCPVC600V | AL3CCPVC5kV | AL3CCPVC15kV
5.5 | 2.6 | 0.05 | 0.063 | 1.2 | 1.2 | 1.2 | 2 | 2 | 2 | 50/60 | W3 |  | 2 | 14 | sq.mm | THHN/THWN | 8 | sq.mm | THHN/THWN | 25mmØ | INSIDE DIAMETER | W3 | 4 | CU | 3 | 8 | 2 | 14 | 389 | - | - | 389 | - | - | 389 | - | - | 389 | - | - | 2 | 14 | 237 | - | - | 237 | - | - | 237 | - | - | 237 | - | -
8 | 3.2 | 0.052 | 0.065 | 0.78 | 0.78 | 0.78 | 1.3 | 1.3 | 1.3 | 70/80 | W4 |  | 2 | 22 | sq.mm | THHN/THWN | 8 | sq.mm | THHN/THWN | 32mmØ | INSIDE DIAMETER | W4 | 5 | CU | 4 | 14 | 3.5 | 12 | 617 | - | - | 617 | - | - | 617 | - | - | 617 | - | - | 3.5 | 12 | 376 | - | - | 376 | - | - | 376 | - | - | 376 | - | -
14 | - | 0.051 | 0.064 | 0.49 | 0.49 | 0.49 | 0.81 | 0.81 | 0.81 | 100 | W5 |  | 2 | 30 | sq.mm | THHN/THWN | 8 | sq.mm | THNN/THWN | 32mmØ | INSIDE DIAMETER | W5 | 6 | CU | 5 | 22 | 5.5 | 10 | 981 | - | - | 982 | - | - | 982 | - | - | 982 | - | - | 5.5 | 10 | 599 | - | - | 599 | - | - | 599 | - | - | 599 | - | -
22 | - | 0.048 | 0.06 | 0.31 | 0.31 | 0.31 | 0.51 | 0.51 | 0.51 | 125 | W6 |  | 2 | 50 | sq.mm | THHN/THWN | 14 | sq.mm | THNN/THWN | 50mmØ | INSIDE DIAMETER | W6 | 8 | CU | 6 | 30 | 8 | 8 | 1557 | 1551 | - | 1559 | 1555 | - | 1559 | 1557 | - | 1560 | 1558 | - | 8 | 8 | 951 | 950 | - | 952 | 951 | - | 952 | 951 | - | 952 | 952 | -
30 | - | 0.045 | 0.057 | 0.19 | 0.2 | 0.2 | 0.32 | 0.32 | 0.32 | 150 | W7 |  | 2 | 60 | sq.mm | THHN/THWN | 14 | sq.mm | THNN/THWN | 50mmØ | INSIDE DIAMETER | W7 | 9 | CU | 7 | 38 | 14 | 6 | 2425 | 2406 | 2389 | 2430 | 2418 | 2407 | 2431 | 2425 | 2415 | 2433 | 2428 | 2421 | 14 | 6 | 1481 | 1476 | 1472 | 1482 | 1479 | 1476 | 1482 | 1480 | 1478 | 1482 | 1481 | 1479
38 | - | 0.046 | 0.057 | 0.15 | 0.16 | 0.16 | 0.25 | 0.26 | 0.25 | 200 | W8 |  | 2 | 80 | sq.mm | THHN/THWN | 22 | sq.mm | THNN/THWN | 50mmØ | INSIDE DIAMETER | W8 | 10 | CU | 8 | 50 | 22 | 4 | 3806 | 3751 | 3696 | 3826 | 3789 | 3753 | 3830 | 3812 | 3779 | 3838 | 3823 | 3798 | 22 | 4 | 2346 | 2333 | 2319 | 2350 | 2342 | 2333 | 2351 | 2347 | 2339 | 2353 | 2350 | 2344
50 | - | 0.044 | 0.055 | 0.12 | 0.13 | 0.12 | 0.2 | 0.21 | 0.2 | 225 | W9 |  | 2 | 100 | sq.mm | THHN/THWN | 30 | sq.mm | THNN/THWN | 65mmØ | INSIDE DIAMETER | W9 | 11 | CU | 9 | 60 | 26 | 3 | 4774 | 4674 | 4577 | 4811 | 4745 | 4679 | 4820 | 4785 | 4726 | 4833 | 4803 | 4762 | 26 | 3 | 2952 | 2928 | 2904 | 2961 | 2945 | 2929 | 2963 | 2955 | 2941 | 2966 | 2959 | 2949
60 | - | 0.043 | 0.054 | 0.1 | 0.1 | 0.1 | 0.16 | 0.16 | 0.16 | 250 | W10 |  | 2 | 125 | sq.mm | THHN/THWN | 30 | sq.mm | THNN/THWN | 65mmØ | INSIDE DIAMETER | W10 | 12 | CU | 10 | 80 | 30 | 2 | 5907 | 5736 | 5574 | 6044 | 5926 | 5809 | 5989 | 5930 | 5828 | 6087 | 6023 | 5958 | 30 | 2 | 3713 | 3670 | 3626 | 3730 | 3702 | 3673 | 3734 | 3719 | 3693 | 3740 | 3725 | 3709
80 | - | 0.042 | 0.052 | 0.077 | 0.082 | 0.079 | 0.13 | 0.13 | 0.13 | 275 | W11 |  | 2 | 150 | sq.mm | THHN/THWN | 30 | sq.mm | THNN/THWN | 80mmØ | INSIDE DIAMETER | W11 | 13 | CU | 11 | 100 | 38 | 1 | 7293 | 7029 | 6759 | 7493 | 7307 | 7109 | 7454 | 7365 | 7189 | 7579 | 7507 | 7364 | 38 | 1 | 4645 | 4575 | 4498 | 4678 | 4632 | 4580 | 4686 | 4664 | 4618 | 4699 | 4682 | 4646
100 | - | 0.041 | 0.051 | 0.062 | 0.067 | 0.063 | 0.1 | 0.11 | 0.1 | 300 | W12 |  | 2 | 200 | sq.mm | THHN/THWN | 30 | sq.mm | THNN/THWN | 80mmØ | INSIDE DIAMETER | W12 | 15 | CU | 12 | 125 | 50 | 1/0 | 8925 | 8544 | 7973 | 9317 | 9034 | 8590 | 9210 | 9086 | 8708 | 9473 | 9373 | 9053 | 50 | 1/0 | 5777 | 5670 | 5493 | 5838 | 5766 | 5646 | 5852 | 5820 | 5717 | 5876 | 5852 | 5771
125 | - | 0.041 | 0.052 | 0.052 | 0.057 | 0.054 | 0.085 | 0.09 | 0.086 | 400 | W13 |  | 2 | 250 | sq.mm | THHN/THWN | 50 | sq.mm | THNN/THWN | 90mmØ | INSIDE DIAMETER | W13 | 16 | CU | 13 | 150 | 60 | 2/0 | 10755 | 10062 | 9390 | 11424 | 10878 | 10319 | 11245 | 11045 | 10500 | 11703 | 11529 | 11053 | 60 | 2/0 | 7187 | 6968 | 6733 | 7301 | 7153 | 6986 | 7327 | 7271 | 7109 | 7373 | 7329 | 7202
150 | - | 0.041 | 0.051 | 0.044 | 0.049 | 0.045 | 0.071 | 0.076 | 0.072 | [12 empty] | X0 | 1 | CU | 14 | 175 | 80 | 3/0 | 12844 | 11804 | 11022 | 13923 | 13048 | 12360 | 13656 | 13333 | 12613 | 14410 | 14119 | 13462 | 80 | 3/0 | 8826 | 8467 | 8163 | 9110 | 8851 | 8627 | 9077 | 8981 | 8751 | 9243 | 9164 | 8977
175 | - | 0.04 | 0.05 | 0.038 | 0.043 | 0.039 | 0.061 | 0.066 | 0.063 | 3 PHASE: 3-WIRE + GROUND : FOR ACCU, EF, PUMP, JF | [11 empty] | X1 | 2 | CU | 15 | 200 | 100 | 4/0 | 15082 | 13606 | 12543 | 16673 | 15351 | 14347 | 16392 | 15890 | 14813 | 17483 | 17020 | 16013 | 100 | 4/0 | 10741 | 10167 | 9700 | 11174 | 10749 | 10387 | 11185 | 11022 | 10642 | 11409 | 11277 | 10969
200 | - | 0.04 | 0.049 | 0.033 | 0.038 | 0.035 | 0.054 | 0.059 | 0.055 | 20 | X0 |  | 3 | 2 | mmØ | THHN/THWN | 2 | mmØ | THNN/THWN | 15mmØ | INSIDE DIAMETER | X2 | 3 | CU | 16 | 250 | 125 | 250 | 16483 | 14925 | 13644 | 18594 | 17121 | 15866 | 18311 | 17851 | 16466 | 19779 | 19352 | 18001 | 125 | 250 | 12122 | 11460 | 10849 | 12862 | 12343 | 11847 | 12797 | 12636 | 12115 | 13236 | 13106 | 12661
250 | - | 0.039 | 0.048 | 0.027 | 0.032 | 0.029 | 0.043 | 0.048 | 0.045 | 30 | X1 |  | 3 | 5.5 | sq.mm | THHN/THWN | 2 | mmØ | THNN/THWN | 20mmØ | INSIDE DIAMETER | X3 | 4 | CU | 17 | 325 | 150 | 300 | 18177 | 16293 | 14769 | 20868 | 18975 | 17409 | 20617 | 20052 | 18319 | 22525 | 21938 | 20163 | 150 | 300 | 13910 | 13009 | 12193 | 14923 | 14183 | 13492 | 14917 | 14698 | 13973 | 15495 | 15300 | 14659
325 | - | 0.039 | 0.048 | 0.023 | 0.028 | 0.025 | 0.036 | 0.041 | 0.038 | 40 | X2 |  | 3 | 8 | sq.mm | THHN/THWN | 5.5 | sq.mm | THNN/THWN | 25mmØ | INSIDE DIAMETER | X4 | 5 | CU | 18 | 375 | 175 | 350 | 19704 | 17385 | 15678 | 22737 | 20526 | 18672 | 22646 | 21914 | 19821 | 24904 | 24126 | 21982 | 175 | 350 | 15484 | 14280 | 13288 | 16813 | 15858 | 14955 | 16795 | 16490 | 15541 | 17635 | 17352 | 16501
375 | - | 0.038 | 0.048 | 0.019 | 0.024 | 0.021 | 0.029 | 0.034 | 0.031 | 50/60 | X3 |  | 3 | 14 | sq.mm | THHN/THWN | 8 | sq.mm | THNN/THWN | 25mmØ | INSIDE DIAMETER | X5 | 6 | CU | 19 | 400 | 200 | 400 | 20566 | 18235 | 16366 | 24297 | 21786 | 19731 | 24253 | 23372 | 21042 | 26916 | 26044 | 23518 | 200 | 400 | 16671 | 15355 | 14188 | 18506 | 17321 | 16234 | 18462 | 18064 | 16921 | 19588 | 19244 | 18154
400 | - | 0.038 | 0.048 | 0.019 | 0.024 | 0.021 | 0.029 | 0.034 | 0.031 | 70/80 | X4 |  | 3 | 22 | sq.mm | THHN/THWN | 8 | sq.mm | THNN/THWN | 32mmØ | INSIDE DIAMETER | X6 | 8 | CU | 20 | 500 | 250 | 500 | 22185 | 19172 | 17492 | 26706 | 23277 | 21330 | 26980 | 25449 | 23126 | 30096 | 28712 | 25916 | 250 | 500 | 18756 | 16828 | 15657 | 21391 | 19503 | 18315 | 21395 | 20607 | 19314 | 23018 | 22381 | 20978
500 | - | 0.037 | 0.046 | 0.015 | 0.019 | 0.018 | 0.023 | 0.027 | 0.025 | 100 | X5 |  | 3 | 30 | sq.mm | THHN/THWN | 8 | sq.mm | THNN/THWN | 32mmØ | INSIDE DIAMETER | X7 | 9 | CU | 31 | 225 | 300 | 600 | 22965 | 20567 | 17962 | 28033 | 25204 | 22097 | 28752 | 27975 | 24897 | 32154 | 31258 | 27766 | 300 | 600 | 20093 | 18428 | 16484 | 23451 | 21718 | 19635 | 23633 | 23196 | 21349 | 25708 | 25244 | 23295
[10 empty] | 125 | X6 |  | 3 | 50 | sq.mm | THHN/THWN | 14 | sq.mm | THNN/THWN | 50mmØ | INSIDE DIAMETER | X8 | 10 | CU | 32 | 400 | 375 | 750 | 24137 | 21387 | 18889 | 29735 | 26453 | 23408 | 31051 | 30024 | 26933 | 34605 | 33315 | 29735 | 375 | 750 | 21766 | 19685 | 17686 | 25976 | 23702 | 21437 | 26432 | 25790 | 23750 | 29036 | 28262 | 25976
[10 empty] | 150 | X7 |  | 3 | 60 | sq.mm | THHN/THWN | 14 | sq.mm | THNN/THWN | 50mmØ | INSIDE DIAMETER | X9 | 11 | CU | 33 | 600 | 500 | 1000 | 25278 | 22539 | 19923 | 31491 | 28083 | 24887 | 33864 | 32689 | 29320 | 37197 | 35749 | 31959 | 500 | 1000 | 23478 | 21235 | 19006 | 28779 | 26109 | 23482 | 29865 | 29049 | 26608 | 32938 | 31920 | 29135
[10 empty] | 200 | X8 |  | 3 | 80 | sq.mm | THHN/THWN | 22 | sq.mm | THNN/THWN | 50mmØ | INSIDE DIAMETER | X10 | 12 | CU | 34 | 800
[10 empty] | 225 | X9 |  | 3 | 100 | sq.mm | THHN/THWN | 30 | sq.mm | THNN/THWN | 65mmØ | INSIDE DIAMETER | X11 | 13 | CU | 35 | 1000
[10 empty] | 250 | X10 |  | 3 | 125 | sq.mm | THHN/THWN | 30 | sq.mm | THNN/THWN | 65mmØ | INSIDE DIAMETER | X12 | 15 | CU | 36 | 1200 | Table 5. “C” Values for Busway
AWG to mm² | [9 empty] | 275 | X11 |  | 3 | 150 | sq.mm | THHN/THWN | 30 | sq.mm | THNN/THWN | 80mmØ | INSIDE DIAMETER | X13 | 16 | CU | 37 | 1350 |  | Busway
[10 empty] | 300 | X12 |  | 3 | 200 | sq.mm | THHN/THWN | 30 | sq.mm | THNN/THWN | 80mmØ | INSIDE DIAMETER | Y0 | 1 | CU | 38 | 1600 | Ampacity | Plug-In | Feeder |  | High Impedance
AWG/ (kcmil) | mm² | mm dia | [7 empty] | 400 | X13 |  | 3 | 250 | sq.mm | THHN/THWN | 50 | sq.mm | THNN/THWN | 90mmØ | INSIDE DIAMETER | Y1 | 2 | CU | 39 | 2000 |  | Copper | Aluminum | Copper | Aluminum | Copper
[22 empty] | Y2 | 3 | CU | 40 | 2500 | 225 | 28700 | 23000 | 18700 | 12000 | —
18 | 0.75 | 1 | [7 empty] | 3 PHASE: 3-WIRE + NEUTRAL + GROUND : FOR MAINS | [11 empty] | Y3 | 4 | CU | 41 | 3000 | 400 | 38900 | 34700 | 23900 | 21300 | —
16 | 1.25 | 1.2 | [7 empty] | 20 | Y0 |  | 4 | 2 | mmØ | THHN/THWN | 2 | mmØ | THNN/THWN | 15mmØ | INSIDE DIAMETER | Y4 | 5 | CU | 42 | 4000 | 600 | 41000 | 38300 | 36500 | 31300 | —
14 | 2 | 1.6 | [7 empty] | 30 | Y1 |  | 4 | 5.5 | sq.mm | THHM/THWN | 2 | mmØ | THNN/THWN | 20mmØ | INSIDE DIAMETER | Y5 | 6 | CU |  |  | 800 | 46100 | 57500 | 49300 | 44100 | —
12 | 3.5 | 2 | [7 empty] | 40 | Y2 |  | 4 | 8 | sq.mm | THHM/THWN | 5.5 | sq.mm | THNN/THWN | 25mmØ | INSIDE DIAMETER | Y6 | 8 | CU |  |  | 1000 | 69400 | 89300 | 62900 | 56200 | 15600
10 | 5.5 | 2.6 | [7 empty] | 50/60 | Y3 |  | 4 | 14 | sq.mm | THHM/THWN | 8 | sq.mm | THNN/THWN | 25mmØ | INSIDE DIAMETER | Y7 | 9 | CU |  |  | 1200 | 94300 | 97100 | 76900 | 69900 | 16100
8 | 8 | 3.2 | [7 empty] | 70/80 | Y4 |  | 4 | 22 | sq.mm | THHM/THWN | 8 | sq.mm | THNN/THWN | 32mmØ | INSIDE DIAMETER | Y8 | 10 | CU |  |  | 1350 | 119000 | 104200 | 90100 | 84000 | 17500
6 | 14 | [8 empty] | 100 | Y5 |  | 4 | 30 | sq.mm | THHM/THWN | 8 | sq.mm | THNN/THWN | 32mmØ | INSIDE DIAMETER | Y9 | 11 | CU | Cable Type |  | 1600 | 129900 | 120500 | 101000 | 90900 | 19200
4 | 22 | [8 empty] | 125 | Y6 |  | 4 | 50 | sq.mm | THHM/THWN | 14 | sq.mm | THNN/THWN | 50mmØ | INSIDE DIAMETER | Y10 | 12 | CU | 3 Single Conductors | 3SC | 2000 | 142900 | 135100 | 134200 | 125000 | 20400
3 | 26 | [8 empty] | 150 | Y7 |  | 4 | 60 | sq.mm | THHM/THWN | 14 | sq.mm | THNN/THWN | 50mmØ | INSIDE DIAMETER | Y11 | 13 | CU | 3 Conductor Cable | 3CC | 2500 | 143800 | 156300 | 180500 | 166700 | 21700
2 | 30 | [8 empty] | 200 | Y8 |  | 4 | 80 | sq.mm | THHM/THWN | 22 | sq.mm | THNN/THWN | 50mmØ | INSIDE DIAMETER | Y12 | 15 | CU | Busduct | - | 3000 | 144900 | 175400 | 204100 | 188700 | 23800
1 | 38 | [8 empty] | 225 | Y9 |  | 4 | 100 | sq.mm | THHM/THWN | 30 | sq.mm | THNN/THWN | 65mmØ | INSIDE DIAMETER | Y13 | 16 | CU |  |  | 4000 | — | — | 277800 | 256400 | —
1/0 | 50 | [8 empty] | 250 | Y10 |  | 4 | 125 | sq.mm | THHM/THWN | 30 | sq.mm | THNN/THWN | 65mmØ | INSIDE DIAMETER | ZX0 | 1 | CU | Conduit Type
2/0 | 60 | [8 empty] | 275 | Y11 |  | 4 | 150 | sq.mm | THHM/THWN | 30 | sq.mm | THNN/THWN | 80mmØ | INSIDE DIAMETER | ZX1 | 2 | CU | Steel | Stl
3/0 | 80 | [8 empty] | 300 | Y12 |  | 4 | 200 | sq.mm | THHM/THWN | 30 | sq.mm | THNN/THWN | 80mmØ | INSIDE DIAMETER | ZX2 | 3 | CU | Nonmagnetic | PVC
4/0 | 100 | [8 empty] | 400 | Y13 |  | 4 | 250 | sq.mm | THHM/THWN | 50 | sq.mm | THNN/THWN | 90mmØ | INSIDE DIAMETER | ZX3 | 4 | CU | N/A | -
250 | 125 | [20 empty] | ZX4 | 5 | CU
300 | 150 | [8 empty] | 3 PHASE (FIRE-RATED OHLS): 3-WIRE + GROUND : FOR FIRE-LIFE SAFETY LOADS | [11 empty] | ZX5 | 6 | CU | Wire Voltage Rating
350 | 175 | [8 empty] | 20 | ZX0 |  | 3 | 2 | mmØ | 3-HOURS FIRE-RATED CU/MICA/XLPE/LSOH CABLES | 2 | mmØ | THNN/THWN | 25mmØ | INSIDE DIAMETER | ZX6 | 8 | CU | 600V
400 | 200 | [8 empty] | 30 | ZX1 |  | 3 | 5.5 | sq.mm | 3-HOURS FIRE-RATED CU/MICA/XLPE/LSOH CABLES | 2 | mmØ | THNN/THWN | 25mmØ | INSIDE DIAMETER | ZX7 | 9 | CU | 5kV
500 | 250 | [8 empty] | 40 | ZX2 |  | 3 | 8 | sq.mm | 3-HOURS FIRE-RATED CU/MICA/XLPE/LSOH CABLES | 5.5 | sq.mm | THNN/THWN | 25mmØ | INSIDE DIAMETER | ZX8 | 10 | CU | 15kV
600 | 300 | [8 empty] | 50/60 | ZX3 |  | 3 | 14 | sq.mm | 3-HOURS FIRE-RATED CU/MICA/XLPE/LSOH CABLES | 8 | sq.mm | THNN/THWN | 25mmØ | INSIDE DIAMETER | ZX9 | 11 | CU | -
700 | 450 | [8 empty] | 70/80 | ZX4 |  | 3 | 22 | sq.mm | 3-HOURS FIRE-RATED CU/MICA/XLPE/LSOH CABLES | 8 | sq.mm | THNN/THWN | 32mmØ | INSIDE DIAMETER | ZX10 | 12 | CU
750 | 375 | [8 empty] | 100 | ZX5 |  | 3 | 30 | sq.mm | 3-HOURS FIRE-RATED CU/MICA/XLPE/LSOH CABLES | 8 | sq.mm | THNN/THWN | 50mmØ | INSIDE DIAMETER | ZX11 | 13 | CU
800 | 400 | [8 empty] | 125 | ZX6 |  | 3 | 50 | sq.mm | 3-HOURS FIRE-RATED CU/MICA/XLPE/LSOH CABLES | 14 | sq.mm | THNN/THWN | 50mmØ | INSIDE DIAMETER | ZX12 | 15 | CU
900 | 450 | [8 empty] | 150 | ZX7 |  | 3 | 60 | sq.mm | 3-HOURS FIRE-RATED CU/MICA/XLPE/LSOH CABLES | 14 | sq.mm | THNN/THWN | 50mmØ | INSIDE DIAMETER | ZX13 | 16 | CU
1000 | 500 | [8 empty] | 200 | ZX8 |  | 3 | 80 | sq.mm | 3-HOURS FIRE-RATED CU/MICA/XLPE/LSOH CABLES | 22 | sq.mm | THNN/THWN | 50mmØ | INSIDE DIAMETER | ZY0 | 1 | CU
1250 | 625 | [8 empty] | 225 | ZX9 |  | 3 | 100 | sq.mm | 3-HOURS FIRE-RATED CU/MICA/XLPE/LSOH CABLES | 30 | sq.mm | THNN/THWN | TRAY |  | ZY1 | 2 | CU
1500 | 750 | [8 empty] | 250 | ZX10 |  | 3 | 125 | sq.mm | 3-HOURS FIRE-RATED CU/MICA/XLPE/LSOH CABLES | 30 | sq.mm | THNN/THWN | TRAY |  | ZY2 | 3 | CU
1750 | 875 | [8 empty] | 275 | ZX11 |  | 3 | 150 | sq.mm | 3-HOURS FIRE-RATED CU/MICA/XLPE/LSOH CABLES | 30 | sq.mm | THNN/THWN | TRAY |  | ZY3 | 4 | CU
2000 | 1000 | [8 empty] | 300 | ZX12 |  | 3 | 200 | sq.mm | 3-HOURS FIRE-RATED CU/MICA/XLPE/LSOH CABLES | 30 | sq.mm | THNN/THWN | TRAY |  | ZY4 | 5 | CU
[10 empty] | 400 | ZX13 |  | 3 | 250 | sq.mm | 3-HOURS FIRE-RATED CU/MICA/XLPE/LSOH CABLES | 50 | sq.mm | THNN/THWN | TRAY |  | ZY5 | 6 | CU
[22 empty] | ZY6 | 8 | CU
[10 empty] | 3 PHASE (FIRE-RATED OHLS): 3-WIRE + NEUTRAL + GROUND : FOR FIRE-LIFE SAFETY LOADS | [11 empty] | ZY7 | 9 | CU
[10 empty] | 20 | ZY0 |  | 4 | 2 | mmØ | 3-HOURS FIRE-RATED CU/MICA/XLPE/LSOH CABLES | 2 | mmØ | THNN/THWN | 25mmØ | INSIDE DIAMETER | ZY8 | 10 | CU
[10 empty] | 30 | ZY1 |  | 4 | 5.5 | sq.mm | 3-HOURS FIRE-RATED CU/MICA/XLPE/LSOH CABLES | 5.5 | sq.mm | THNN/THWN | 32mmØ | INSIDE DIAMETER | ZY9 | 11 | CU
[10 empty] | 40 | ZY2 |  | 4 | 8 | sq.mm | 3-HOURS FIRE-RATED CU/MICA/XLPE/LSOH CABLES | 5.5 | sq.mm | THNN/THWN | 32mmØ | INSIDE DIAMETER | ZY10 | 12 | CU
[10 empty] | 50/60 | ZY3 |  | 4 | 14 | sq.mm | 3-HOURS FIRE-RATED CU/MICA/XLPE/LSOH CABLES | 8 | sq.mm | THNN/THWN | 32mmØ | INSIDE DIAMETER | ZY11 | 13 | CU
[10 empty] | 70/80 | ZY4 |  | 4 | 22 | sq.mm | 3-HOURS FIRE-RATED CU/MICA/XLPE/LSOH CABLES | 8 | sq.mm | THNN/THWN | 32mmØ | INSIDE DIAMETER | ZY12 | 15 | CU
[10 empty] | 100 | ZY5 |  | 4 | 30 | sq.mm | 3-HOURS FIRE-RATED CU/MICA/XLPE/LSOH CABLES | 8 | sq.mm | THNN/THWN | 50mmØ | INSIDE DIAMETER | ZY13 | 16 | CU
[10 empty] | 125 | ZY6 |  | 4 | 50 | sq.mm | 3-HOURS FIRE-RATED CU/MICA/XLPE/LSOH CABLES | 14 | sq.mm | THNN/THWN | 50mmØ | INSIDE DIAMETER | AX9 | 11 | AL
[10 empty] | 150 | ZY7 |  | 4 | 60 | sq.mm | 3-HOURS FIRE-RATED CU/MICA/XLPE/LSOH CABLES | 14 | sq.mm | THNN/THWN | 50mmØ | INSIDE DIAMETER | AX10 | 12 | AL
[10 empty] | 200 | ZY8 |  | 4 | 80 | sq.mm | 3-HOURS FIRE-RATED CU/MICA/XLPE/LSOH CABLES | 22 | sq.mm | THNN/THWN | 50mmØ | INSIDE DIAMETER | AX11 | 13 | AL
[10 empty] | 225 | ZY9 |  | 4 | 100 | sq.mm | 3-HOURS FIRE-RATED CU/MICA/XLPE/LSOH CABLES | 30 | sq.mm | THNN/THWN | TRAY |  | AX12 | 15 | AL
[10 empty] | 250 | ZY10 |  | 4 | 125 | sq.mm | 3-HOURS FIRE-RATED CU/MICA/XLPE/LSOH CABLES | 30 | sq.mm | THNN/THWN | TRAY |  | AX13 | 16 | AL
[10 empty] | 275 | ZY11 |  | 4 | 150 | sq.mm | 3-HOURS FIRE-RATED CU/MICA/XLPE/LSOH CABLES | 30 | sq.mm | THNN/THWN | TRAY |  | AX14 | 17 | AL
[10 empty] | 300 | ZY12 |  | 4 | 200 | sq.mm | 3-HOURS FIRE-RATED CU/MICA/XLPE/LSOH CABLES | 30 | sq.mm | THNN/THWN | TRAY |  | 2AX12 | 15 | AL
[10 empty] | 400 | ZY13 |  | 4 | 250 | sq.mm | 3-HOURS FIRE-RATED CU/MICA/XLPE/LSOH CABLES | 50 | sq.mm | THNN/THWN | TRAY |  | 2AX14 | 17 | AL
[22 empty] | AY9 | 11 | AL
[10 empty] | 3 PHASE (ALUMINUM): 3-WIRE + GROUND : MAINS (SIZE≈2×DIA. OF COPPER) | [11 empty] | AY10 | 12 | AL
[10 empty] | 125 | AX9 |  | 3 | 100 | sq.mm | THHN/THWN | 30 | sq.mm | THHN/THWN | 80mm | INSIDE DIAMETER | AY11 | 13 | AL
[10 empty] | 150 | AX10 |  | 3 | 125 | sq.mm | THHN/THWN | 50 | sq.mm | THHN/THWN | 80mm | INSIDE DIAMETER | AY12 | 15 | AL
[10 empty] | 175 | AX11 |  | 3 | 150 | sq.mm | THHN/THWN | 50 | sq.mm | THHN/THWN | 90mm | INSIDE DIAMETER | AY13 | 16 | AL
[10 empty] | 200 | AX12 |  | 3 | 200 | sq.mm | THHN/THWN | 60 | sq.mm | THHN/THWN | 100mm | INSIDE DIAMETER | AY14 | 17 | AL
[10 empty] | 250 | AX13 |  | 3 | 250 | sq.mm | THHN/THWN | 80 | sq.mm | THHN/THWN | 100mm | INSIDE DIAMETER | 2AY12 | 15 | AL
[10 empty] | 300 | AX14 |  | 3 | 325 | sq.mm | THHN/THWN | 100 | sq.mm | THHN/THWN | 100mm | INSIDE DIAMETER | 2AY13 | 17 | AL
[10 empty] | 400 | 2AX12 | 2 | 3 | 125 | sq.mm | THHN/THWN | 30 | sq.mm | THHN/THWN | 100mm | INSIDE DIAMETER | BC-W1 | 3 | CU
[10 empty] | 600 | 2AX14 | 3 | 3 | 125 | sq.mm | THHN/THWN | 30 | sq.mm | THHN/THWN | 100mm | INSIDE DIAMETER | BC-W2 | 4 | CU
[22 empty] | BC-W3 | 5 | CU
[10 empty] | 3 PHASE (ALUMINUM): 3-WIRE + NEUTRAL + GROUND : MAINS (SIZE≈2×DIA. OF COPPER) | [11 empty] | BC-W4 | 6 | CU
[10 empty] | 125 | AY9 |  | 4 | 100 | sq.mm | THHN/THWN | 30 | sq.mm | THHN/THWN | 80mm | INSIDE DIAMETER | BC-W5 | 8 | CU
[10 empty] | 150 | AY10 |  | 4 | 125 | sq.mm | THHN/THWN | 50 | sq.mm | THHN/THWN | 80mm | INSIDE DIAMETER | BC-W6 | 9 | CU
[10 empty] | 175 | AY11 |  | 4 | 150 | sq.mm | THHN/THWN | 50 | sq.mm | THHN/THWN | 90mm | INSIDE DIAMETER | BC-W7 | 10 | CU
[10 empty] | 200 | AY12 |  | 4 | 200 | sq.mm | THHN/THWN | 60 | sq.mm | THHN/THWN | 100mm | INSIDE DIAMETER | BC-W8 | 11 | CU
[10 empty] | 250 | AY13 |  | 4 | 250 | sq.mm | THHN/THWN | 80 | sq.mm | THHN/THWN | 100mm | INSIDE DIAMETER | BC-W9 | 12 | CU
[10 empty] | 300 | AY14 |  | 4 | 325 | sq.mm | THHN/THWN | 100 | sq.mm | THHN/THWN | 100mm | INSIDE DIAMETER | BC-W10 | 13 | CU
[10 empty] | 400 | 2AY12 | 2 | 4 | 125 | sq.mm | THHN/THWN | 30 | sq.mm | THHN/THWN | 100mm | INSIDE DIAMETER | BC-Y1 | 3 | CU
[10 empty] | 600 | 2AY13 | 2 | 4 | 125 | sq.mm | THHN/THWN | 30 | sq.mm | THHN/THWN | 100mm | INSIDE DIAMETER | BC-Y2 | 4 | CU
[22 empty] | BC-Y3 | 5 | CU
[10 empty] | 1 PHASE (BRANCH CABLE): 2-WIRE + GROUND | [11 empty] | BC-Y4 | 6 | CU
[10 empty] | 70 | BC-W1 |  | 2 | 10 | sq.mm | Cu PRE-FABRICATED BRANCH CABLE | 8 | sq.mm | THHN/THWN |  |  | BC-Y5 | 8 | CU
[10 empty] | 80 | BC-W2 |  | 2 | 16 | sq.mm | Cu PRE-FABRICATED BRANCH CABLE | 8 | sq.mm | THHN/THWN |  |  | BC-Y6 | 9 | CU
[10 empty] | 125 | BC-W3 |  | 2 | 25 | sq.mm | Cu PRE-FABRICATED BRANCH CABLE | 8 | sq.mm | THHN/THWN |  |  | BC-Y7 | 10 | CU
[10 empty] | 150 | BC-W4 |  | 2 | 35 | sq.mm | Cu PRE-FABRICATED BRANCH CABLE | 14 | sq.mm | THHN/THWN |  |  | BC-Y8 | 11 | CU
[10 empty] | 200 | BC-W5 |  | 2 | 50 | sq.mm | Cu PRE-FABRICATED BRANCH CABLE | 14 | sq.mm | THHN/THWN |  |  | BC-Y9 | 12 | CU
[10 empty] | 250 | BC-W6 |  | 2 | 70 | sq.mm | Cu PRE-FABRICATED BRANCH CABLE | 22 | sq.mm | THHN/THWN |  |  | BC-Y10 | 13 | CU
[10 empty] | 300 | BC-W7 |  | 2 | 95 | sq.mm | Cu PRE-FABRICATED BRANCH CABLE | 30 | sq.mm | THHN/THWN |  |  | BUS-CU1 | 31 | BUS-CU
[10 empty] | 350 | BC-W8 |  | 2 | 120 | sq.mm | Cu PRE-FABRICATED BRANCH CABLE | 30 | sq.mm | THHN/THWN |  |  | BUS-CU2 | 32 | BUS-CU
[10 empty] | 400 | BC-W9 |  | 2 | 150 | sq.mm | Cu PRE-FABRICATED BRANCH CABLE | 30 | sq.mm | THHN/THWN |  |  | BUS-CU3 | 33 | BUS-CU
[10 empty] | 500 | BC-W10 |  | 2 | 186 | sq.mm | Cu PRE-FABRICATED BRANCH CABLE | 30 | sq.mm | THHN/THWN |  |  | BUS-CU4 | 34 | BUS-CU
[22 empty] | BUS-CU5 | 35 | BUS-CU
[10 empty] | 3 PHASE (BRANCH CABLE): 3-WIRE + NEUTRAL + GROUND | [11 empty] | BUS-CU6 | 36 | BUS-CU
[10 empty] | 70 | BC-Y1 |  | 2 | 10 | sq.mm | Cu PRE-FABRICATED BRANCH CABLE | 8 | sq.mm | THHN/THWN |  |  | BUS-CU7 | 37 | BUS-CU
[10 empty] | 80 | BC-Y2 |  | 2 | 16 | sq.mm | Cu PRE-FABRICATED BRANCH CABLE | 8 | sq.mm | THHN/THWN |  |  | BUS-CU8 | 38 | BUS-CU
[10 empty] | 125 | BC-Y3 |  | 2 | 25 | sq.mm | Cu PRE-FABRICATED BRANCH CABLE | 8 | sq.mm | THHN/THWN |  |  | BUS-CU9 | 39 | BUS-CU
[10 empty] | 150 | BC-Y4 |  | 2 | 35 | sq.mm | Cu PRE-FABRICATED BRANCH CABLE | 14 | sq.mm | THHN/THWN |  |  | BUS-CU10 | 40 | BUS-CU
[10 empty] | 200 | BC-Y5 |  | 2 | 50 | sq.mm | Cu PRE-FABRICATED BRANCH CABLE | 14 | sq.mm | THHN/THWN |  |  | BUS-CU11 | 41 | BUS-CU
[10 empty] | 250 | BC-Y6 |  | 2 | 70 | sq.mm | Cu PRE-FABRICATED BRANCH CABLE | 22 | sq.mm | THHN/THWN |  |  | BUS-CU12 | 42 | BUS-CU
[10 empty] | 300 | BC-Y7 |  | 2 | 95 | sq.mm | Cu PRE-FABRICATED BRANCH CABLE | 30 | sq.mm | THHN/THWN |  |  | BUS-AL1 | 31 | BUS-AL
[10 empty] | 350 | BC-Y8 |  | 2 | 120 | sq.mm | Cu PRE-FABRICATED BRANCH CABLE | 30 | sq.mm | THHN/THWN |  |  | BUS-AL2 | 32 | BUS-AL
[10 empty] | 400 | BC-Y9 |  | 2 | 150 | sq.mm | Cu PRE-FABRICATED BRANCH CABLE | 30 | sq.mm | THHN/THWN |  |  | BUS-AL3 | 33 | BUS-AL
[10 empty] | 500 | BC-Y10 |  | 2 | 186 | sq.mm | Cu PRE-FABRICATED BRANCH CABLE | 30 | sq.mm | THHN/THWN |  |  | BUS-AL4 | 34 | BUS-AL
[22 empty] | BUS-AL5 | 35 | BUS-AL
[22 empty] | BUS-AL6 | 36 | BUS-AL
[22 empty] | BUS-AL7 | 37 | BUS-AL
[22 empty] | BUS-AL8 | 38 | BUS-AL
[22 empty] | BUS-AL9 | 39 | BUS-AL
[22 empty] | BUS-AL10 | 40 | BUS-AL
[22 empty] | BUS-AL11 | 41 | BUS-AL
[22 empty] | BUS-AL12 | 42 | BUS-AL

## Tests
AWG to mm²
AWG | mm² | mm dia
- | #REF! | #REF! | or Conduit Conduit
kcmil Steel Nonmagnetic Steel Nonmagnetic
600V 5kV 15kV 600V 5kV 15kV 600V 5kV 15kV 600V 5kV 15kV
14 389 - - 389 - - 389 - - 389 - -
12 617 - - 617 - - 617 - - 617 - -
10 981 - - 982 - - 982 - - 982 - -
8 1557 1551 - 1559 1555 - 1559 1557 - 1560 1558 -
6 2425 2406 2389 2430 2418 2407 2431 2425 2415 2433 2428 2421
4 3806 3751 3696 3826 3789 3753 3830 3812 3779 3838 3823 3798
3 4774 4674 4577 4811 4745 4679 4820 4785 4726 4833 4803 4762
2 5907 5736 5574 6044 5926 5809 5989 5930 5828 6087 6023 5958
1 7293 7029 6759 7493 7307 7109 7454 7365 7189 7579 7507 7364
1/0 8925 8544 7973 9317 9034 8590 9210 9086 8708 9473 9373 9053
2/0 10755 10062 9390 11424 10878 10319 11245 11045 10500 11703 11529 11053
3/0 12844 11804 11022 13923 13048 12360 13656 13333 12613 14410 14119 13462
4/0 15082 13606 12543 16673 15351 14347 16392 15890 14813 17483 17020 16013
250 16483 14925 13644 18594 17121 15866 18311 17851 16466 19779 19352 18001
300 18177 16293 14769 20868 18975 17409 20617 20052 18319 22525 21938 20163
350 19704 17385 15678 22737 20526 18672 22646 21914 19821 24904 24126 21982
400 20566 18235 16366 24297 21786 19731 24253 23372 21042 26916 26044 23518
500 22185 19172 17492 26706 23277 21330 26980 25449 23126 30096 28712 25916
600 22965 20567 17962 28033 25204 22097 28752 27975 24897 32154 31258 27766
750 24137 21387 18889 29735 26453 23408 31051 30024 26933 34605 33315 29735
1,000 25278 22539 19923 31491 28083 24887 33864 32689 29320 37197 35749 31959
Aluminum
14 237 - - 237 - - 237 - - 237 - -
12 376 - - 376 - - 376 - - 376 - -
10 599 - - 599 - - 599 - - 599 - -
8 951 950 - 952 951 - 952 951 - 952 952 -
6 1481 1476 1472 1482 1479 1476 1482 1480 1478 1482 1481 1479
4 2346 2333 2319 2350 2342 2333 2351 2347 2339 2353 2350 2344
|  |  | 3 2952 2928 2904 2961 2945 2929 2963 2955 2941 2966 2959 2949 | -
2 3713 3670 3626 3730 3702 3673 3734 3719 3693 3740 3725 3709
1 4645 4575 4498 4678 4632 4580 4686 4664 4618 4699 4682 4646
1/0 5777 5670 5493 5838 5766 5646 5852 5820 5717 5876 5852 5771
2/0 7187 6968 6733 7301 7153 6986 7327 7271 7109 7373 7329 7202
3/0 8826 8467 8163 9110 8851 8627 9077 8981 8751 9243 9164 8977
4/0 10741 10167 9700 11174 10749 10387 11185 11022 10642 11409 11277 10969
250 12122 11460 10849 12862 12343 11847 12797 12636 12115 13236 13106 12661
300 13910 13009 12193 14923 14183 13492 14917 14698 13973 15495 15300 14659
350 15484 14280 13288 16813 15858 14955 16795 16490 15541 17635 17352 16501
400 16671 15355 14188 18506 17321 16234 18462 18064 16921 19588 19244 18154
500 18756 16828 15657 21391 19503 18315 21395 20607 19314 23018 22381 20978
600 20093 18428 16484 23451 21718 19635 23633 23196 21349 25708 25244 23295
750 21766 19685 17686 25976 23702 21437 26432 25790 23750 29036 28262 25976
1,000 23478 21235 19006 28779 26109 23482 29865 29049 26608 32938 31920 29135
Ampacity Busway
Plug-In Feeder High Impedance
Copper Aluminum Copper Aluminum Copper
225 28700 23000 18700 12000 —
400 38900 34700 23900 21300 —
600 41000 38300 36500 31300 —
800 46100 57500 49300 44100 —
1000 69400 89300 62900 56200 15600
1200 94300 97100 76900 69900 16100
1350 119000 104200 90100 84000 17500
1600 129900 120500 101000 90900 19200
2000 142900 135100 134200 125000 20400
2500 143800 156300 180500 166700 21700
3000 144900 175400 204100 188700 23800
4000 — — 277800 256400 —